## UFLS (Cat1&Cat2) (hidden)
UNDER-FREQUENCY LOAD SHEDDING (UFLS) REVISION 2024
Assignment | GM - Subzone | Substation | Mnemonic | kV | Assigned Feeders | CB | Freq1 | Delay1 (s) | Freq2 | Delay2 (s) | MW Quantum 2024 | Load Area Affected | UFLS 2024 Review Remarks
Stage: Ride Through Total load: 311MW | Kuantan | Gebeng Industri | GBID | 132 | KSTL 1 & 2 | 105 & 405 | 49.3 | 0 | n/a | n/a | 0 | KSTL load
| Johor Bahru | Tanjung Langsat | TLST | 132 | TLTP (Titan Petrochemicals) | 505 | 49.3 | 0 | n/a | n/a | 26 | TLTP
| Johor Bahru | Pasir Gudang Darat | PGDT | 132 | TTAN 1 & 2 | 905 & 1005 | 49.3 | 0 | n/a | n/a | 28 | TTAN
| Johor Bahru | Pasir Gudang Ind Est | PGIE | 132 | ASTM 1 & 2 | 805 & 905 | 49.3 | 0 | n/a | n/a | 2 | ASTM
| Johor Bahru | Tanjung Langsat Industrial Estate | TLIE | 275 | BSTL 1 & 2 | L15 & L25 | 49.3 | 0 | n/a | n/a | 7 | BSTL
| Kuantan | Tanjung Gelang | TGLN | 132 | JDSI 1 & 2 | 505 & 605 | 49.3 | 0 | n/a | n/a | 0 | JDSI
| Dungun | Telok Kalong | TKLG | 275 | Perwaja 1 & 2 | L15 & L25 | 49.3 | 1 | n/a | n/a | 0 | PWSM
| Selangor | Olak Lempit | OLPT | 275 | MGST 1 & 2 | L75 & L85 | 49.3 | 0 | n/a | n/a | 25 | MGST
| Selangor | Bukit Raja GIS | BRGS | 132 | ASMB 1 & 2 | 11130, 11230, 11330 | 49.3 | 0 | n/a | n/a | 44 | ASMB
| Selangor | Bukit Raja GIS | BRGS | 132 | MSWK | 7130, 7230 | 49.3 | 0 | n/a | n/a | 60 | MSWK
| Perda | Bukit Tengah | BTGH | 132 | SRON 2 | 905 | 49.3 | 0 | n/a | n/a | 50 | SRON 905 only
| Perda | Bedong | BDNG | 275 | PWGR 1 & 2 feeders | L35 & L45 | 49.3 | 0 | n/a | n/a | 6 | PWGR
| Perda | Prai Industrial | PRID | 132 | SRON & SRNW | 505 & 605 | 49.3 | 0 | n/a | n/a | 17 | SRON & SRNW
| Perda | SKS Prai | SKSP | 132 | MWTA 1 & 2 | 105 & 205 | 49.3 | 0 | n/a | n/a | 46 | MWTA
Stage 1: 49.2Hz Total load: 1001MW | Johor Bahru | Cahaya Baru | CBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 21.3659 | CBRU 22kV
| Johor Bahru | Pasir Gudang Darat | PGDT | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 21.8789 | PGDT 22kV
| Johor Bahru | Tampoi Industries | TMPI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 64.0768 | TMPI 33kV
| Perda | Sungai Ara (GIS) | SARA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 41.5461 | SARA 33kV
| Kuantan | Pekan Industri AIP | PKNI | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a | 18.5562 | PKNI 33kV
| Ayer Keroh | Hicom Pegoh | HPGH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 15.3861 | HPGH 33kV
| Seremban | Enstek | ESTK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 36.4197 | ESTK 33kV
| Seremban | Kg. Repah | KRPH | 11 | 132/11kV T1 & T2 | 30 & 32 | 49.2 | 0 | n/a | n/a | 20.2233 | KRPH 11kV
| Ipoh | Pengkalan Industri | PKID | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a | 21.5372 | PKID 11kV
| Ipoh | Pengkalan Industri | PKID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 25.2821 | PKID 33kV
| Ipoh | Kinta Valley Resort | KVRT | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.2 | 0 | n/a | n/a | 61.5771 | KVRT 33 kV
| Ipoh | Menglembu | MLBU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 83.9211 | MLBU 33kV
| Selangor | Setia Alam | STIA | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a | 76.0234 | STIA 33kV
| Kuala Lumpur | Damansara City | DCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 28.4475 | DCTY 33kV
| Kuala Lumpur | Manjalara | MJLR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 89.8683 | MJLR 33kV
| Kuala Lumpur | Sri Hartamas | SHMS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 71.0055 | SHMS 33kV
| Kuala Lumpur | Suncity GIS | SCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T2 | 49.2 | 0 | n/a | n/a | 25.6995 | SCTY 33kV
| Kuala Lumpur | Cheras Jaya | CJYA | 33 | 132/33kV T1, T2 & T3 | 1T0 & 2T0 & 3T0 | 49.2 | 0 | n/a | n/a | 157.1371 | CJYA 33kV
| Kuala Lumpur | Danau Desa | DDSA | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 60.7924 | DDSA 33kV
| Alor Setar | Mergong | MGON | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a | 17.2107 | MGON 11kV
| Alor Setar | Pauh | PAUH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 42.691 | PAUH 33kV
Stage 2: 49.1Hz Total load: 801MW | Ipoh | Temoh | TMOH | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.1 | 0 | n/a | n/a | 22.3732 | TMOH 33kV
| Ipoh | Kelebang | KLBG | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.1 | 0 | n/a | n/a | 24.6724 | KLBG 33kV
| Ipoh | New Khantan | NKAN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 32.1433 | NKAN 33kV
| Ipoh | Tasik | TASK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 8.5343 | TASK 22kV
| Kuala Lumpur | SPPK Cheras | SPKC | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 1W0 & 5T0 | 49.1 | 0 | n/a | n/a | 123.2475 | SPKC 33kV
| Kuala Lumpur | National University | NUNI | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 24.5161 | NUNI 11kV
| Johor Bahru | Plentong | PLTG | 230 | WAV8 1 & 2 | H10 & H20 | 49.1 | 0 | n/a | n/a | - | TNB-Singapore Interconnection
| Johor Bahru | Tebrau | TBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 29.3428 | TBRU 22kV
| Kuantan | Kampung Awah | KAWA | 132 | KRYG 1 & 2 | 305 & 405 | 49.1 | 0 | n/a | n/a | 30 | KRYG
| Seremban | Tuanku Jaafar (GIS) | TJGS | 132 | SHEL 1 & 2 | 505 & 605 | 49.1 | 0 | n/a | n/a | 36 | SHELL
| Selangor | Hicom | HCOM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 77.918 | HCOM 33 kV
| Selangor | Shah Alam East | SHAE | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 49.1 | 0 | n/a | n/a | 72.8698 | SHAE 33kV
| Selangor | Shah Alam South | SHAS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 64 | SHAS 33kV
| Kota Bharu | Panchor | PCOR | 33 | 132/33kV T2 & T3 & T4 | 2T0, 3T0 & 4T0 | 49.1 | 0 | n/a | n/a | 67.9031 | PCOR 33kV | Category 2: New assignment (to include 2T0)
| Kluang | Johor Tengah | JTGH | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 20.2863 | JTGH 11kV
| Perda | Seberang Jaya | SJAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 74.3213 | SJAY 33kV
| Perda | Taman Intan | INTN | 33 | 132/33kV T3 & T4 | 3T0&4T0 | 49.1 | 0 | n/a | n/a | 51.9714 | INTN 33kV
| Perda | Taman Intan | INTN | 11 | 132/11kV T1 & T2 | 31&32 | 49.1 | 0 | n/a | n/a | 31.6547 | INTN 22kV
| Ayer Keroh | Malacca Power Station | MPSS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 9.404 | MPSS 11kV
Stage 3: 49.0Hz Total load: 977MW | Kota Bharu | Tunjung | TJUG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 60 | TJUG 33kV | Category 2: New assignment (replacement for TMRH: KKRI & MACG defeated due to LSS in the pocket load)
| Ayer Keroh | Malim Jaya | MJYA | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 26.877 | MJYA 11kV
| Ayer Keroh | Muar | MUAR | 11 | 132/11kV T2 & T3 | 32 & 33 | 49 | 0 | n/a | n/a | 32.3916 | MUAR 11kV
| Selangor | Bukit Rajah | BRGS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 18.9852 | BRGS 11 kV
| Selangor | Port Klang P/S | PKLG | 132 | IGBK 1 & 2 | 705 & 805 | 49 | 0 | n/a | n/a | 130 | IGBK & NKST
| Selangor | Bukit Beruntung | BBTG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 41.8364 | BBTG 33kV
| Kuantan | Bandar Indra Mahkota | BIMK | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 28.0406 | BIMK 11kV
| Kuantan | Bandar Indra Mahkota | BIMK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 98.0819 | BIMK 33kV
| Kuantan | Bentong | BNTG | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 23.208 | BNTG 11kV
| Perda | Butterworth North | BWTN | 33 | 132/33 kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 92 | BWTN 33kV
| Perda | Butterworth North | BWTN | 11 | 132/11kV T5 | 35 | 49 | 0 | n/a | n/a | 0 | BWTN 11kV
| Perda | Prai GIS | PRGS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 61.6121 | PRGS 33 kV
| Kuala Lumpur | Serdang Raya | SRDR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 85.1885 | SRDR 33kV
| Kuala Lumpur | Ampang GIS | AMPG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 75.8672 | AMPG T3&T4
| Kuala Lumpur | Air Hitam | AHTM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 65.0735 | AHTM 33kV
| Kuala Lumpur | Bukit Jalil | BJLL | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 85.6804 | BJLL 33kV
| Kuala Lumpur | Balakong | BLKG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 52.1303 | BLKG 33 kV
Stage 4: 48.9Hz Total load: 754MW | Kota Bharu | Kota Bharu | KBRU | 33 | 132/33kV T1 & T3 & T5 | 1T0 & 3T0 & 5T0 | 48.9 | 0 | n/a | n/a | 82.5745 | KBRU 33kV
| Selangor | PJ South | PJST | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 65.7207 | PJST 33 kV | Category 1: Reassignment of operating stage (Freq1: 48.8Hz --> 48.9Hz)
| Kluang | Pasir Gudang Town Centre | PGTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 111.1269 | PGTC 33kV | Category 1: Reassignment of operating stage (Freq1: 49.2Hz --> 48.9Hz)
| Johor Bahru | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 37.2708 | PGIE 22kV
| Johor Bahru | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T3 | 3T0 | 48.9 | 0 | n/a | n/a | 15.0562 | PGIE 22kV
| Selangor | Puchong Jaya | PCHJ | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 83.0514 | PCHJ 33kV
| Selangor | New Subang Uda | NSDA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 62.5762 | NSDA 33 kV
| Kuala Lumpur | Sri Damansara | SDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 67.9905 | SDAM 33kV | Category 1: Reassignment of the operating stage (Freq1: 49.0Hz --> 48.9Hz)
| Kuala Lumpur | New SEA Park | NSPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 68.1678 | NSPK 33 kV
| Kuala Lumpur | Serdang New | SRDN | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.9 | 0 | n/a | n/a | 51.941 | SRDN 33kV
| Seremban | Sendayan | SDYN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 64.8369 | SDYN 33kV | Category 1: Reassignment of the operating stage (Freq1: 49.1Hz --> 48.9Hz)
| Seremban | Lukut | LKUT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.9 | 0 | n/a | n/a | 17.6596 | LKUT 11kV
| Kuantan | Tanjong Gelang | TGLN | 11 | 132/11kV T1 & T2 & T3 | 31 & 32 & 33 | 48.9 | 0 | n/a | n/a | 25.8429 | TGLN 11kV
Stage 5: 48.8Hz Total load: 713MW | Alor Setar | Kota Setar | KSTR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a | 25.7531 | KSTR 11kV
| Kuala Lumpur | Kg Chempaka | KCPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 71.7948 | KCPK 33kV
| Selangor | New Rawang | NRWG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 74.945 | NRWG 33 kV
| Selangor | Bukit Kapar | BKPR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a | 69.4631 | BKPR 33kV
| Selangor | Temasya | TMSY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 60.1524 | TMSY 33 kV
| Ayer Keroh | Kelemak | KLMK | 132 | MTNH 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | 49 | TKMG, PPJG, MTNH
| Seremban | Rantau | RTAU | 132 | TKMG 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a
| Seremban | Paroi | PROI | 132 | TJID 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | 140 | TJID, TTJF, SSUN & STRA
| Seremban | Rasah | RASA | 132 | Satria & TTJF | 505 & 605 | 48.8 | 0 | n/a | n/a
| Kuantan | Bentong South | BNTS | 132 | BNTG & RBDR | 205 & 405 | 48.8 | 0 | n/a | n/a | 133 | BNTA, KLIP, JNKA, JTUT, RBDR | Category 2: New assignment - add JTUT 705
| Kuantan | Kg. Awah | KAWA | 132 | JNKA & JTUT | 205 & 705 | 48.8 | 0 | n/a | n/a
| Perda | Air terjun | ATJN | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a | 56.7503 | ATJN 33 kV
| Perda | Gurun | GRUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a | 9.3912 | GRUN 11kV
| Perda | Jeniang | JENG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 22.7999 | JENG 33kV
Stage 6: 48.7Hz Total load: 931MW | Ipoh | Lumut | LMUT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 58.1226 | LMUT 33kV
| Ipoh | Lumut Maritime | LMTM | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 72.3964 | LMTM 33kV
| Kuala Lumpur | Mutiara Damansara | MDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 38.9019 | MDAM 33kV
| Kuala Lumpur | Batu Caves | BCVS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 84.9599 | BCVS 33kV
| Kluang | Parit Raja | PRJA | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 17.3238 | PRJA 11kV
| Kluang | Yong Peng North | YGPN | 132 | CAAH & BSPT/BKPG | 105 & 205 | 48.7 | 0 | n/a | n/a | 298 | LKJG, XNSS, XNYI, TKID, TKAK, JMTH, SGMT, BSPT, BKPG, CAAH, BAHA, NSCI, GMAS, PBSR, KLPH, SPTG, KKWG | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
| Seremban | Paroi | PROI | 132 | KPLH 1 & 2 | 705 & 805 | 48.7 | 0 | n/a | n/a
| Ayer Keroh | Lipat Kajang | LKJG | 132 | JSIN & MCOP | 505 & 605 | 48.7 | 0 | n/a | n/a
| Ayer Keroh | Ujong Pasir | UPSR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 18 | UPSR 11kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
| Ayer Keroh | Ujong Pasir | UPSR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 60 | UPSR 33kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
| Ayer Keroh | Metacorp | MCOP | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 30 | MCOP 11kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
| Ayer Keroh | Metacorp | MCOP | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 61 | MCOP 33kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
| Seremban | Nilai | NLAI | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 22.8675 | NLAI 11kV | Category 1: Reassignment of operating stage (Freq1: 48.9Hz --> 48.7Hz)
| Selangor | Batu Tiga | BTGA | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.7 | 0 | n/a | n/a | 71.3972 | BTGA 33kV
| Selangor | Bukit Badong | BBDG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 66.6988 | BBDG 33kV
| Selangor | Rasa Selangor Industry | RSID | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 31.7609 | RSID 11kV
Stage 7: 48.6Hz Total load: 906MW | Ayer Keroh | Gerisik | GRSK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 21.3927 | GRSK 11kV
| Johor Bahru | Kota Putri | KPTR | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 35.0813 | KPTR 22kV
| Johor Bahru | Skudai | SDAI | 22 | 132/22kV T7 & T8 | 37 & 38 | 48.6 | 0 | n/a | n/a | 1.4469 | SDAI 22kV | Category 1: Reassignment of operating stage (Freq1: 48.2Hz --> 48.6Hz) and removing setting Freq2 (Freq2: 49.3Hz @ 90s --> n/a)
| Johor Bahru | Larkin GIS | LKIN | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 33.3325 | LKIN 22kV
| Kuantan | Kg. Awah | KAWA | 132 | SONG | 605 | 48.6 | 0 | n/a | n/a | 90 | SONG, MTKB, TMID, MNID
| Kuantan | Jambu Rias | JBRS | 132 | TMID | 205 | 48.6 | 0 | n/a | n/a
| Perda | Gelugor | GLGR | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.6 | 0 | n/a | n/a | 61.1334 | GLGR 33kV
| Perda | Bayan Mutiara | BMTR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 105.8642 | BMTR 33kV
| Perda | Batu Kawan South | BTWS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 52.4377 | BTWS 33kV
| Perlis | Kangar | KGAR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 14.2995 | KGAR 33kV
| Selangor | Shah Alam West | SHAW | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 69.0504 | SHAW 33kV
| Selangor | Shah Alam West | SHAW | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 15.0282 | SHAW 11kV
| Selangor | Teluk Panglima Garang | TPGR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 98.751 | TPGR 33kV
| Selangor | Shah Alam North | SHAN | 11 | 132/11kV T1, T2 & T3 | 31, 32 & 33 | 48.6 | 0 | n/a | n/a | 4.0549 | SHAN 11kV
| Selangor | Shah Alam Section 18 GIS | SHLB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 77.1695 | SHLB 33kV | Category 1: Reassignment of operating stage (Freq1: 48.5Hz --> 48.6Hz)
| Selangor | Bandar Botanic | BBTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 81.8867 | BBTC 33kV | Category 1: Reassignment removing setting for Freq2 (Freq2: 49.3Hz @ 120s --> n/a)
| Perda | Bedong | BDNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 45.0985 | BDNG 33kV | Category 1: Reassignment of operating stage (Freq1: 48.7Hz --> 48.6Hz)
| Kuala Lumpur | Kuala Lumpur North | KULN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 71.6655 | KULN 33kV
| Terengganu | Dungun | DGUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 9.9042 | DGUN 11kV
| Terengganu | Chendering | CHRG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 18.4411 | CHRG 11kV
Stage 8: 48.5Hz Total load: 916MW | Kluang | Kluang (New) | KLUG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 20.3434 | KLUG 11kV
| Johor Bahru | Majidee | MAJD | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 34.6464 | MAJD 22kV
| Terengganu | Dungun Industries | DGID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 17.7645 | DGID 33kV
| Terengganu | Chukai | CKAI | 33 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 16.51 | CKAI 11kV
| Alor Setar | Tanjong Pauh | PAUH | 11 | 132/11kV T3 & T4 | 35 & 36 | 48.5 | 0 | n/a | n/a | 20.2035 | PAUH 11kV
| Perda | Bukit Minyak | BMYK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 40.4944 | BMYK 11kV
| Perda | Bukit Minyak | BMYK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 99.6068 | BMYK 33kV
| Perda | Prai Industries | PRID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 70.4984 | PRID 33kV
| Perda | Prai Industries | PRID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 99.1207
| Selangor | Puchong Perdana | PCHP | 33 | 132/33kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.5 | 0 | n/a | n/a | 96.6747 | PCHP 33kV
| Selangor | Connaught Bridge PS | CBPS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 127.7547 | CBPS 33kV
| Selangor | Bandar Baru Shah Alam | SHAB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 90.9176 | SHAB 33kV | Category 1: Reassignment of operating stage (Freq1: 48.4Hz --> 48.5Hz)
| Kuala Lumpur | Segambut | SGBT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 81.4331 | SGBT 33kV
| Kota Bharu | Jeli | JELI | 33 | 275/33kV T1 & T2 | 1T0 & 2T1 | 48.5 | 0 | n/a | n/a | 16.6814 | JELI 33kV
| Kota Bharu | Tanah Merah | TMRH | 132 | Pasir Putih 1 & 2 | 305 & 405 | 48.5 | 0 | n/a | n/a | 83 | PPTH & SJTH
| Kota Bharu | Kandis | KDIS | 132 | Pasir Putih 1 & 2 | 505 & 605 | 48.5 | 0 | n/a | n/a
Stage 9: 48.4Hz Total load: 858MW | Ayer Keroh | Kelemak | KLMK | 132 | CHNG & ZRNA | 305 & 805 | 48.4 | 0 | n/a | n/a | 268 | ZRNA, SPWR, CHNG, BMKA, MMKA, BVTA, MFDR, TGBU, PPSR, HLNM, BRBI
| Ayer Keroh | Malim Jaya | MJYA | 132 | BVTA 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a
| Ayer Keroh | Malacca | MCCA | 132 | BRBI 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a
| Ayer Keroh | Malacca | MCCA | 132 | TGBU 1 & 2 | 905 & 1005 | 48.4 | 0 | n/a | n/a
| Terengganu | Kenyir Temporary | KNYT | 132 | KBRG & CHRG/KTGU | 305 & 205 | 48.4 | 0 | n/a | n/a | 153 | GBDK, KBRG, KTGU & BRKT | *GM to confirm the current relay installations post new KNYT configuration
| Terengganu | Chendering | CHRG | 132 | KBRG/KTGU & KNYT/KTGU | 205 & 305 | 48.4 | 0 | n/a | n/a
| Kluang | Bukit Batu | BBTU | 132 | SNAI & SLNG | 205 & 505 | 48.4 | 0 | n/a | n/a | 232 | SLNG, SNAI, KLAI & UTMJ
| Johor Bahru | Skudai | SDAI | 132 | SNAI & SLNG | 305 & 405 | 48.4 | 0 | n/a | n/a
| Selangor | Batang Berjuntai | BTAI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 14.7682 | BTAI 33kV
| Kuala Lumpur | K.L.East | KULE | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 61.6353 | KULE 33kV
| Kuala Lumpur | KL Pavilion | KLPV | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 68.7869 | KLPV 33kV
| Perda | Tikam Batu | TKBU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 60.3016 | TKBU 33kV
Stage 10: 48.3Hz Total load: 852MW | Johor Bahru | Tampoi | TPOI | 22 | 132/22kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120 | 35.9347 | TPOI 22kV
| Kluang | Batu Pahat East | BPHE | 132 | BPHT 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120 | 41 | BPHT, TPCH
| Kluang | Yong Peng | YGPG | 132 | BPHT & TPCH | 105 & 205 | 48.3 | 0 | 49.3 | 120
| Kluang | Yong Peng | YGPG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120 | - | YGPG 11kV
| Selangor | Jalan Meru | MERU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.3 | 0 | 49.3 | 120 | 100.9312 | MERU 33 kV
| Selangor | Proton | PROT | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120 | 115.4056 | PROT 33kV
| Seremban | Kilat | KLAT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120 | 21.521 | KLAT 11kV
| Alor Setar | Perlis Power Station | PLPS | 132 | TPAU | 705 | 48.3 | 0 | 49.3 | 120 | 96 | TPAU, TEWA, UMKA, KCMT
| Alor Setar | Kuala Perlis | KPLS | 132 | TEWA 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120
| Kuala Lumpur | Imbi | IMBI | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120 | 91.9517 | IMBI 33 kV
| Kuala Lumpur | Kota Damansara | KDSA | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120 | 148.4245 | KDSA 33kV
| Kuala Lumpur | Galloway | GWAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.3 | 0 | 49.3 | 120 | 57.1456 | GWAY 33kV | Category 1: Reassignment of operating stage (Freq1: 48.2Hz --> 48.3Hz) and (Freq2: 49.3Hz @90s --> 49.3Hz @120)
| Perda | Bukit Tambun | BTBN | 132 | VDOR/JNKO & NBTL Feeders | 105 & 205 | 48.3 | 0 | 49.3 | 120 | 144 | JNKO, VDOR, PBTR, NBTL | Category 2: New assignment (replacement for BMRH: BSRI 1 & 2 defeated due to LSS KNLS in the pocket load)
| Perda | Bagan Serai | BSRI | 132 | PBTR & NBTL | 105 & 205 | 48.3 | 0 | 49.3 | 120
Stage 11: 48.2Hz Total load: 688MW | Perda | Sungai Pinang | SPNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90 | 80.5657 | SPNG 33kV
| Seremban | Nilai | NLAI | 132 | MTIN & AMID | 505 & 605 | 48.2 | 0 | 49.3 | 90 | 285 | MTIN, AMID, BRNG, SMYH, BHGT, PJAM
| Seremban | Paroi | PROI | 132 | MTIN 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
| Kuala Lumpur | Kajang | KJNG | 132 | KEST 1 & 2 | 105 & 205 | 48.2 | 0 | 49.3 | 90
| Kuala Lumpur | National University | NUNI | 132 | BHGT 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
| Kuala Lumpur | Bukit Mahkamah | BMKM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90 | 51.7312 | BMKM 33kV
| Johor Bahru | Tebrau | TBRU | 132 | PLGI 1 & 2 | 905 & 1005 | 48.2 | 0 | 49.3 | 90 | 152 | KTGI, UTRM, PUBB, PLGI | *GM to confirm the current relay installation (previous network configuration were UTRM & KTGI)
| Johor Bahru | Pasak | PSAK | 132 | PUBB & KTGI | 505 & 605 | 48.2 | 0 | 49.3 | 90
| Kluang | Renggam | RNGM | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.2 | 0 | 49.3 | 90 | 7.3649 | RNGM 11kV
| Kluang | Kluang | KLUG | 132 | KLID & NYOR | 105 & 205 | 48.2 | 0 | 49.3 | 90 | 111 | KLID, MSNG, TGMK & NYOR
Stage 12: 48.1Hz Total load: 466MW | Alor Setar | Kangar | KGAR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 33.8944 | KGAR 11kV
| Ipoh | Sri Iskandar | SIKD | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 & 1W0 | 48.1 | 0 | 49.3 | 60 | 30.6965 | SIKD 33kV
| Selangor | Ladang Kundang | LKDG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.1 | 0 | 49.3 | 60 | 36.7625 | LKDG 33kV
| Selangor | Subang Jaya Town Centre | SJTC | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.1 | 0 | 49.3 | 60 | 54.0023 | SJTC 33kV
| Perda | Bayan Baru | BBRU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60 | 98.3955 | BBRU 33kV
| Seremban | Semarak | SMRK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 22.9899 | SMRK 11kV
| Seremban | Semarak | SMRK | 132 | Hualon 1, 2 & 3 | 505605705 | 48.1 | 0 | 49.3 | 60 | 40 | HLNN
| Johor Bahru | Seelong | SELG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 21.4779 | SELG 11kV
| Johor Bahru | Stulang Darat | STUL | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60 | 22.8338 | STUL 22kV
| Kluang | Batu Pahat East | BPHE | 132 | SGAD 1 & 2 | 105 & 205 | 48.1 | 0 | 49.3 | 60 | 105 | SGAD, PJML, PYSF, PSRI & SSLG
| Ayer Keroh | Sungai Abong | SABG | 132 | PJML & PYSF | 305 & 405 | 48.1 | 0 | 49.3 | 60

## UFLS (Cat3 Deactivate) (hidden)
UNDER-FREQUENCY LOAD SHEDDING (UFLS) REVISION 2024
GM - Subzone | Substation | Mnemonic | kV | Assigned Feeders | CB | UFLS 2024 Review Remarks
Dungun | Telok Kalong | TKLG | 275 | ESTL 1 & 2 | L95 & L105 | Deactivate for the latest 2024 review
Kota Bharu | Tanah Merah | TMRH | 132 | KKRI 1&2 | 505 & 605 | Deactivate for latest the 2024 review due to LSS MALS and the future Nenggiri Power Station in the pocket load
Melaka | Ujong Pasir | UPSR | 132 | AKRH & AKRH/ONST | 105 & 205 | Deactivate for latest the 2024 review due to LSS JSLS in the pocket load
Kuala Lumpur | Bandar Tun Razak | BTRZ | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 & 1W0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 19 Aug 2022
Kuala Lumpur | KL City Centre | KLCC | 11 | 132/11kV T1 & T2 | 31 & 32 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 19 Aug 2022
Kuala Lumpur | Putrajaya | PJYC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated Nov 2022
Perda | Bukit Merah | BMRH | 132 | BSRI 1 & 2 | 305 & 405 | Deactivate for latest the 2024 review due to LSS KNLS in the pocket load
Perda | Bayan Lepas | BLPS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 19 Aug 2022
Perda | Bayan Lepas | BLPS | 33 | 132/33kV T3 & T5 | 3T0 & 4T0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 19 Aug 2022
Perda | Bayan Baru | BBRU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 19 Aug 2022
Perda | Bedong | BDNG | 132 | SPID & AJYA | 105 & 205 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 19 Aug 2022
Kuala Lumpur | Kajang | KJNG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Kuala Lumpur | Pandan Maju | PMJU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Kuala Lumpur | Pandan Maju | PMJU | 33 | 132/33kV T5 & T6 | 5T0 & 6T0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Selangor | Banting | BTIN | 132 | OLPT1 & 2 | 505 & 605 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Selangor | Bukit Changgang | BCHG | 132 | BTIN/SGLC 1 & 2 | 105 & 205 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Selangor | Port Klang P/S | PKLG | 132 | KSGR & SBSR | 105 & 405 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Ipoh | Temoh | TMOH | 132 | KGJH 1 & 2 | 105 & 205 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Ipoh | Lumut | LMUT | 132 | KGJH 1 & 2 | 305 & 405 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Ipoh | Bukit Merah | BMRH | 132 | PKCB & KMTG | 105 & 205 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Ipoh | Kuala Kangsar | KKSR | 132 | TPID & TPSS | 905 & 1005 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Alor Setar | Alor Star | ASTR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Kluang | Batu Pahat East | BPHE | 132 | TLBH & RNGT | 505 & 805 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Johor Bahru | Gelang Patah | GPTH | 132 | TKPG 1 & 2 | 305 & 405 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Johor Bahru | Skudai | SDAI | 132 | TUNI & PNAS | 905 & 1005 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Seremban | Rasah | RASA | 11 | 132/11 kV T1 & T2 | 31 & 32 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Kuantan | Kampung Awah | KAWA | 132 | MRAN & MECC | 505 & 805 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020
Kuantan | Kuantan | KTAN | 132 | KTNN feeders | 305 & 405 | Deactivate. Supplying to essential loads - TNB/GSO/GSM/GST/3/1 (UFLS/UVLS) dated 6 April 2020

## ActiveAll_UFLS&UVLS (hidden)
UNDER-FREQUENCY LOAD SHEDDING (UFLS) | [13 empty] | UNDER-VOLTAGE LOAD SHEDDING (UVLS)
Assignment | GM - Subzone | Substation | Mnemonic | kV | Assigned Feeders | CB | Freq1 | Delay1 (s) | Freq2 | Delay2 (s) | MW Quantum 2024 | Load Area Affected | UFLS 2024 Review Remarks | Voltage pickup setting (p.u) | Delay (s) | UVLS Operating Stage
Stage: Ride Through | Kuantan | Gebeng Industri | GBID | 132 | KSTL 1 & 2 | 105 & 405 | 49.3 | 0 | n/a | n/a | 0 | KSTL load
Stage: Ride Through | Johor Bahru | Tanjung Langsat | TLST | 132 | TLTP (Titan Petrochemicals) | 505 | 49.3 | 0 | n/a | n/a | 26 | TLTP
Stage: Ride Through | Johor Bahru | Pasir Gudang Darat | PGDT | 132 | TTAN 1 & 2 | 905 & 1005 | 49.3 | 0 | n/a | n/a | 28 | TTAN
Stage: Ride Through | Johor Bahru | Pasir Gudang Ind Est | PGIE | 132 | ASTM 1 & 2 | 805 & 905 | 49.3 | 0 | n/a | n/a | 2 | ASTM
Stage: Ride Through | Johor Bahru | Tanjung Langsat Industrial Estate | TLIE | 275 | BSTL 1 & 2 | L15 & L25 | 49.3 | 0 | n/a | n/a | 7 | BSTL
Stage: Ride Through | Kuantan | Tanjung Gelang | TGLN | 132 | JDSI 1 & 2 | 505 & 605 | 49.3 | 0 | n/a | n/a | 0 | JDSI
Stage: Ride Through | Dungun | Telok Kalong | TKLG | 275 | Perwaja 1 & 2 | L15 & L25 | 49.3 | 1 | n/a | n/a | 0 | PWSM
Stage: Ride Through | Selangor | Olak Lempit | OLPT | 275 | MGST 1 & 2 | L75 & L85 | 49.3 | 0 | n/a | n/a | 25 | MGST
Stage: Ride Through | Selangor | Bukit Raja GIS | BRGS | 132 | ASMB 1 & 2 | 11130, 11230, 11330 | 49.3 | 0 | n/a | n/a | 44 | ASMB
Stage: Ride Through | Selangor | Bukit Raja GIS | BRGS | 132 | MSWK | 7130, 7230 | 49.3 | 0 | n/a | n/a | 60 | MSWK
Stage: Ride Through | Perda | Bukit Tengah | BTGH | 132 | SRON 2 | 905 | 49.3 | 0 | n/a | n/a | 50 | SRON 905 only
Stage: Ride Through | Perda | Bedong | BDNG | 275 | PWGR 1 & 2 feeders | L35 & L45 | 49.3 | 0 | n/a | n/a | 6 | PWGR
Stage: Ride Through | Perda | Prai Industrial | PRID | 132 | SRON & SRNW | 505 & 605 | 49.3 | 0 | n/a | n/a | 17 | SRON & SRNW
Stage: Ride Through | Perda | SKS Prai | SKSP | 132 | MWTA 1 & 2 | 105 & 205 | 49.3 | 0 | n/a | n/a | 46 | MWTA
Stage 1: 49.2Hz | Johor Bahru | Cahaya Baru | CBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 21.3659 | CBRU 22kV
Stage 1: 49.2Hz | Johor Bahru | Pasir Gudang Darat | PGDT | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 21.8789 | PGDT 22kV
Stage 1: 49.2Hz | Johor Bahru | Tampoi Industries | TMPI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 64.0768 | TMPI 33kV
Stage 1: 49.2Hz | Perda | Sungai Ara (GIS) | SARA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 41.5461 | SARA 33kV
Stage 1: 49.2Hz | Kuantan | Pekan Industri AIP | PKNI | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a | 18.5562 | PKNI 33kV
Stage 1: 49.2Hz | Ayer Keroh | Hicom Pegoh | HPGH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 15.3861 | HPGH 33kV
Stage 1: 49.2Hz | Seremban | Enstek | ESTK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 36.4197 | ESTK 33kV
Stage 1: 49.2Hz | Seremban | Kg. Repah | KRPH | 11 | 132/11kV T1 & T2 | 30 & 32 | 49.2 | 0 | n/a | n/a | 20.2233 | KRPH 11kV
Stage 1: 49.2Hz | Ipoh | Pengkalan Industri | PKID | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a | 21.5372 | PKID 11kV
Stage 1: 49.2Hz | Ipoh | Pengkalan Industri | PKID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 25.2821 | PKID 33kV
Stage 1: 49.2Hz | Ipoh | Kinta Valley Resort | KVRT | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.2 | 0 | n/a | n/a | 61.5771 | KVRT 33 kV
Stage 1: 49.2Hz | Ipoh | Menglembu | MLBU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 83.9211 | MLBU 33kV
Stage 1: 49.2Hz | Selangor | Setia Alam | STIA | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a | 76.0234 | STIA 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Damansara City | DCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 28.4475 | DCTY 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Manjalara | MJLR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 89.8683 | MJLR 33kV |  | 0.9 | 30 | 1
Stage 1: 49.2Hz | Kuala Lumpur | Sri Hartamas | SHMS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 71.0055 | SHMS 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Suncity GIS | SCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T2 | 49.2 | 0 | n/a | n/a | 25.6995 | SCTY 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Cheras Jaya | CJYA | 33 | 132/33kV T1, T2 & T3 | 1T0 & 2T0 & 3T0 | 49.2 | 0 | n/a | n/a | 157.1371 | CJYA 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Danau Desa | DDSA | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 60.7924 | DDSA 33kV
Stage 1: 49.2Hz | Alor Setar | Mergong | MGON | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a | 17.2107 | MGON 11kV
Stage 1: 49.2Hz | Alor Setar | Pauh | PAUH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 42.691 | PAUH 33kV
Stage 2: 49.1Hz | Ipoh | Temoh | TMOH | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.1 | 0 | n/a | n/a | 22.3732 | TMOH 33kV
Stage 2: 49.1Hz | Ipoh | Kelebang | KLBG | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.1 | 0 | n/a | n/a | 24.6724 | KLBG 33kV
Stage 2: 49.1Hz | Ipoh | New Khantan | NKAN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 32.1433 | NKAN 33kV
Stage 2: 49.1Hz | Ipoh | Tasik | TASK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 8.5343 | TASK 22kV
Stage 2: 49.1Hz | Kuala Lumpur | SPPK Cheras | SPKC | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 1W0 & 5T0 | 49.1 | 0 | n/a | n/a | 123.2475 | SPKC 33kV
Stage 2: 49.1Hz | Kuala Lumpur | National University | NUNI | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 24.5161 | NUNI 11kV
Stage 2: 49.1Hz | Johor Bahru | Plentong | PLTG | 230 | WA18 1 & 2 | H10 & H20 | 49.1 | 0 | n/a | n/a | - | TNB-Singapore Interconnection
Stage 2: 49.1Hz | Johor Bahru | Tebrau | TBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 29.3428 | TBRU 22kV
Stage 2: 49.1Hz | Kuantan | Kampung Awah | KAWA | 132 | KRYG 1 & 2 | 305 & 405 | 49.1 | 0 | n/a | n/a | 30 | KRYG
Stage 2: 49.1Hz | Seremban | Tuanku Jaafar (GIS) | TJGS | 132 | SHEL 1 & 2 | 505 & 605 | 49.1 | 0 | n/a | n/a | 36 | SHELL
Stage 2: 49.1Hz | Selangor | Hicom | HCOM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 77.918 | HCOM 33 kV
Stage 2: 49.1Hz | Selangor | Shah Alam East | SHAE | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 49.1 | 0 | n/a | n/a | 72.8698 | SHAE 33kV
Stage 2: 49.1Hz | Selangor | Shah Alam South | SHAS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 64 | SHAS 33kV
Stage 2: 49.1Hz | Kota Bharu | Panchor | PCOR | 33 | 132/33kV T2 & T3 & T4 | 2T0, 3T0 & 4T0 | 49.1 | 0 | n/a | n/a | 67.9031 | PCOR 33kV | Category 2: New assignment (to include 2T0)
Stage 2: 49.1Hz | Kluang | Johor Tengah | JTGH | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 20.2863 | JTGH 11kV
Stage 2: 49.1Hz | Perda | Seberang Jaya | SJAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 74.3213 | SJAY 33kV
Stage 2: 49.1Hz | Perda | Taman Intan | INTN | 33 | 132/33kV T3 & T4 | 3T0&4T0 | 49.1 | 0 | n/a | n/a | 51.9714 | INTN 33kV
Stage 2: 49.1Hz | Perda | Taman Intan | INTN | 11 | 132/11kV T1 & T2 | 31&32 | 49.1 | 0 | n/a | n/a | 31.6547 | INTN 22kV
Stage 2: 49.1Hz | Ayer Keroh | Malacca Power Station | MPSS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 9.404 | MPSS 11kV
Stage 3: 49.0Hz | Kota Bharu | Tunjang | TJUG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 60 | TJUG 33kV | Category 2: New assignment (replacement for TMRH: KKRI & MACG defeated due to LSS in the pocket load)
Stage 3: 49.0Hz | Ayer Keroh | Malim Jaya | MJYA | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 26.877 | MJYA 11kV
Stage 3: 49.0Hz | Ayer Keroh | Muar | MUAR | 11 | 132/11kV T2 & T3 | 32 & 33 | 49 | 0 | n/a | n/a | 32.3916 | MUAR 11kV
Stage 3: 49.0Hz | Selangor | Bukit Rajah | BRGS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 18.9852 | BRGS 11 kV
Stage 3: 49.0Hz | Selangor | Port Klang P/S | PKLG | 132 | IGBK 1 & 2 | 705 & 805 | 49 | 0 | n/a | n/a | 130 | IGBK & NKST
Stage 3: 49.0Hz | Selangor | Bukit Beruntung | BBTG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 41.8364 | BBTG 33kV
Stage 3: 49.0Hz | Kuantan | Bandar Indra Mahkota | BIMK | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 28.0406 | BIMK 11kV
Stage 3: 49.0Hz | Kuantan | Bandar Indra Mahkota | BIMK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 98.0819 | BIMK 33kV
Stage 3: 49.0Hz | Kuantan | Bentong | BNTG | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 23.208 | BNTG 11kV
Stage 3: 49.0Hz | Perda | Butterworth North | BWTN | 33 | 132/33 kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a |  | BWTN 33kV
Stage 3: 49.0Hz | Perda | Butterworth North | BWTN | 11 | 132/11kV T5 | 35 | 49 | 0 | n/a | n/a |  | BWTN 11kV
Stage 3: 49.0Hz | Perda | Prai GIS | PRGS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 61.6121 | PRGS 33 kV
Stage 3: 49.0Hz | Kuala Lumpur | Serdang Raya | SRDR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 85.1885 | SRDR 33kV
Stage 3: 49.0Hz | Kuala Lumpur | Ampang GIS | AMPG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 75.8672 | AMPG T3&T4
Stage 3: 49.0Hz | Kuala Lumpur | Air Hitam | AHTM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 65.0735 | AHTM 33kV
Stage 3: 49.0Hz | Kuala Lumpur | Bukit Jalil | BJLL | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 85.6804 | BJLL 33kV
Stage 3: 49.0Hz | Kuala Lumpur | Balakong | BLKG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 52.1303 | BLKG 33 kV
Stage 4: 48.9Hz | Kota Bharu | Kota Bharu | KBRU | 33 | 132/33kV T1 & T3 & T5 | 1T0 & 3T0 & 5T0 | 48.9 | 0 | n/a | n/a | 82.5745 | KBRU 33kV
Stage 4: 48.9Hz | Selangor | PJ Selatan | PJST | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 65.7207 | PJST 33 kV | Category 1: Reassignment of operating stage (Freq1: 48.8Hz --> 48.9Hz)
Stage 4: 48.9Hz | Kluang | Pasir Gudang Town Centre | PGTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 111.1269 | PGTC 33kV | Category 1: Reassignment of operating stage (Freq1: 49.2Hz --> 48.9Hz)
Stage 4: 48.9Hz | Johor Bahru | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 37.2708 | PGIE 22kV
Stage 4: 48.9Hz | Johor Bahru | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T3 | 3T0 | 48.9 | 0 | n/a | n/a | 15.0562 | PGIE 22kV
Stage 4: 48.9Hz | Selangor | Puchong Jaya | PCHJ | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 83.0514 | PCHJ 33kV
Stage 4: 48.9Hz | Selangor | New Subang Uda | NSDA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 62.5762 | NSDA 33 kV
Stage 4: 48.9Hz | Kuala Lumpur | Sri Damansara | SDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 67.9905 | SDAM 33kV | Category 1: Reassignment of the stage (Freq1: 49.0Hz --> 48.9Hz) | 0.9 | 60 | 2
Stage 4: 48.9Hz | Kuala Lumpur | New SEA Park | NSPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 68.1678 | NSPK 33 kV |  | 0.9 | 90 | 3
Stage 4: 48.9Hz | Kuala Lumpur | Serdang New | SRDN | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.9 | 0 | n/a | n/a | 51.941 | SRDN 33kV
Stage 4: 48.9Hz | Seremban | Sendayan | SDYN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 64.8369 | SDYN 33kV | Category 1: Reassignment of the stage (Freq1: 49.1Hz --> 48.9Hz)
Stage 4: 48.9Hz | Seremban | Lukut | LKUT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.9 | 0 | n/a | n/a | 17.6596 | LKUT 11kV
Stage 4: 48.9Hz | Kuantan | Tanjong Gelang | TGLN | 11 | 132/11kV T1 & T2 & T3 | 31 & 32 & 33 | 48.9 | 0 | n/a | n/a | 25.8429 | TGLN 11kV
Stage 5: 48.8Hz | Alor Setar | Kota Setar | KSTR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a | 25.7531 | KSTR 11kV
Stage 5: 48.8Hz | Kuala Lumpur | Kg Chempaka | KCPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 71.7948 | KCPK 33kV |  | 0.9 | 30 | 1
Stage 5: 48.8Hz | Selangor | New Rawang | NRWG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 74.945 | NRWG 33 kV |  | 0.9 | 90 | 3
Stage 5: 48.8Hz | Selangor | Bukit Kapar | BKPR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a | 69.4631 | BKPR 33kV
Stage 5: 48.8Hz | Selangor | Temasya | TMSY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 60.1524 | TMSY 33 kV
Stage 5: 48.8Hz | Ayer Keroh | Kelemak | KLMK | 132 | MTNH 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | 49 | TKMG, PPJG, MTNH
Stage 5: 48.8Hz | Seremban | Rantau | RTAU | 132 | TKMG 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a
Stage 5: 48.8Hz | Seremban | Paroi | PROI | 132 | TJID 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | 140 | TJID, TTJF, SSUN & STRA
Stage 5: 48.8Hz | Seremban | Rasah | RASA | 132 | Satria & TTJF | 505 & 605 | 48.8 | 0 | n/a | n/a
Stage 5: 48.8Hz | Kuantan | Bentong South | BNTS | 132 | BNTG & RBDR | 205 & 405 | 48.8 | 0 | n/a | n/a | 133 | BNTA, KLIP, JNKA, JTUT, RBDR | Category 2: New assignment - add JTUT 705
Stage 5: 48.8Hz | Kuantan | Kg. Awah | KAWA | 132 | JNKA & JTUT | 205 & 705 | 48.8 | 0 | n/a | n/a
Stage 5: 48.8Hz | Perda | Air terjun | ATJN | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a | 56.7503 | ATJN 33 kV
Stage 5: 48.8Hz | Perda | Gurun | GRUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a | 9.3912 | GRUN 11kV
Stage 5: 48.8Hz | Perda | Jeniang | JENG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 22.7999 | JENG 33kV
Stage 6: 48.7Hz | Ipoh | Lumut | LMUT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 58.1226 | LMUT 33kV
Stage 6: 48.7Hz | Ipoh | Lumut Maritime | LMTM | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 72.3964 | LMTM 33kV
Stage 6: 48.7Hz | Kuala Lumpur | Mutiara Damansara | MDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 38.9019 | MDAM 33kV
Stage 6: 48.7Hz | Kuala Lumpur | Batu Caves | BCVS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 84.9599 | BCVS 33kV |  | 0.9 | 90 | 3
Stage 6: 48.7Hz | Kluang | Parit Raja | PRJA | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 17.3238 | PRJA 11kV
Stage 6: 48.7Hz | Kluang | Yong Peng North | YGPN | 132 | CAAH & BSPT/BKPG | 105 & 205 | 48.7 | 0 | n/a | n/a | 298 | LKJG, XNSS, XNYI, TKID, TKAK, JMTH, SGMT, BSPT, BKPG, CAAH, BAHA, NSCI, GMAS, PBSR, KLPH, SPTG, KKWG | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Seremban | Paroi | PROI | 132 | KPLH 1 & 2 | 705 & 805 | 48.7 | 0 | n/a | n/a
Stage 6: 48.7Hz | Ayer Keroh | Lipat Kajang | LKJG | 132 | JSIN & MCOP | 505 & 605 | 48.7 | 0 | n/a | n/a
Stage 6: 48.7Hz | Ayer Keroh | Ujong Pasir | UPSR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 18 | UPSR 11kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Ayer Keroh | Ujong Pasir | UPSR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 60 | UPSR 33kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Ayer Keroh | Metacorp | MCOP | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 30 | MCOP 11kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Ayer Keroh | Metacorp | MCOP | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 61 | MCOP 33kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Seremban | Nilai | NLAI | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 22.8675 | NLAI 11kV | Category 1: Reassignment of operating stage (Freq1: 48.9Hz --> 48.7Hz)
Stage 6: 48.7Hz | Selangor | Batu Tiga | BTGA | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.7 | 0 | n/a | n/a | 71.3972 | BTGA 33kV
Stage 6: 48.7Hz | Selangor | Bukit Badong | BBDG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 66.6988 | BBDG 33kV
Stage 6: 48.7Hz | Selangor | Rasa Selangor Industry | RSID | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 31.7609 | RSID 11kV
Stage 7: 48.6Hz | Ayer Keroh | Gerisik | GRSK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 21.3927 | GRSK 11kV
Stage 7: 48.6Hz | Johor Bahru | Kota Putri | KPTR | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 35.0813 | KPTR 22kV
Stage 7: 48.6Hz | Johor Bahru | Skudai | SDAI | 22 | 132/22kV T7 & T8 | 37 & 38 | 48.6 | 0 | n/a | n/a | 1.4469 | SDAI 22kV | Category 1: Reassignment of operating stage (Freq1: 48.2Hz --> 48.6Hz) and removing setting Freq2 (Freq2: 49.3Hz @ 90s --> n/a)
Stage 7: 48.6Hz | Johor Bahru | Larkin GIS | LKIN | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 33.3325 | LKIN 22kV |  | 0.9 | 30 | 1
Stage 7: 48.6Hz | Kuantan | Kg. Awah | KAWA | 132 | SONG | 605 | 48.6 | 0 | n/a | n/a | 90 | SONG, MTKB, TMID, MNID
Stage 7: 48.6Hz | Kuantan | Jambu Rias | JBRS | 132 | TMID | 205 | 48.6 | 0 | n/a | n/a
Stage 7: 48.6Hz | Perda | Gelugor | GLGR | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.6 | 0 | n/a | n/a | 61.1334 | GLGR 33kV
Stage 7: 48.6Hz | Perda | Bayan Mutiara | BMTR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 105.8642 | BMTR 33kV
Stage 7: 48.6Hz | Perda | Batu Kawan South | BTWS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 52.4377 | BTWS 33kV
Stage 7: 48.6Hz | Alor Setar | Kangar | KGAR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 14.2995 | KGAR 33kV
Stage 7: 48.6Hz | Selangor | Shah Alam West | SHAW | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 69.0504 | SHAW 33kV
Stage 7: 48.6Hz | Selangor | Shah Alam West | SHAW | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 15.0282 | SHAW 11kV
Stage 7: 48.6Hz | Selangor | Teluk Panglima Garang | TPGR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 98.751 | TPGR 33kV
Stage 7: 48.6Hz | Selangor | Shah Alam North | SHAN | 11 | 132/11kV T1, T2 & T3 | 31, 32 & 33 | 48.6 | 0 | n/a | n/a | 4.0549 | SHAN 11kV
Stage 7: 48.6Hz | Selangor | Shah Alam Section 18 GIS | SHLB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 77.1695 | SHLB 33kV | Category 1: Reassignment of operating stage (Freq1: 48.5Hz --> 48.6Hz)
Stage 7: 48.6Hz | Selangor | Bandar Botanic | BBTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 81.8867 | BBTC 33kV | Category 1: Reassignment removing setting for Freq2 (Freq2: 49.3Hz @ 120s --> n/a)
Stage 7: 48.6Hz | Perda | Bedong | BDNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 45.0985 | BDNG 33kV | Category 1: Reassignment of operating stage (Freq1: 48.7Hz --> 48.6Hz)
Stage 7: 48.6Hz | Kuala Lumpur | Kuala Lumpur North | KULN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 71.6655 | KULN 33kV
Stage 7: 48.6Hz | Dungun | Dungun | DGUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 9.9042 | DGUN 11kV
Stage 7: 48.6Hz | Dungun | Chendering | CHRG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 18.4411 | CHRG 11kV
Stage 8: 48.5Hz | Kluang | Kluang (New) | KLUG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 20.3434 | KLUG 11kV
Stage 8: 48.5Hz | Johor Bahru | Majidee | MAJD | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 34.6464 | MAJD 22kV |  | 0.9 | 60 | 2
Stage 8: 48.5Hz | Dungun | Dungun Industries | DGID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 17.7645 | DGID 33kV
Stage 8: 48.5Hz | Dungun | Chukai | CKAI | 33 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 16.51 | CKAI 11kV
Stage 8: 48.5Hz | Alor Setar | Tanjong Pauh | PAUH | 11 | 132/11kV T3 & T4 | 35 & 36 | 48.5 | 0 | n/a | n/a | 20.2035 | PAUH 11kV
Stage 8: 48.5Hz | Perda | Bukit Minyak | BMYK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 40.4944 | BMYK 11kV
Stage 8: 48.5Hz | Perda | Bukit Minyak | BMYK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 99.6068 | BMYK 33kV |  | 0.9 | 30 | 1
Stage 8: 48.5Hz | Perda | Prai Industries | PRID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 70.4984 | PRID 33kV
Stage 8: 48.5Hz | Perda | Prai Industries | PRID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 99.1207
Stage 8: 48.5Hz | Selangor | Puchong Perdana | PCHP | 33 | 132/33kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.5 | 0 | n/a | n/a | 96.6747 | PCHP 33kV
Stage 8: 48.5Hz | Selangor | Connaught Bridge PS | CBPS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 127.7547 | CBPS 33kV
Stage 8: 48.5Hz | Selangor | Bandar Baru Shah Alam | SHAB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 90.9176 | SHAB 33kV | Category 1: Reassignment of operating stage (Freq1: 48.4Hz --> 48.5Hz)
Stage 8: 48.5Hz | Kuala Lumpur | Segambut | SGBT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 81.4331 | SGBT 33kV |  | 0.9 | 30 | 1
Stage 8: 48.5Hz | Kota Bharu | Jeli | JELI | 33 | 275/33kV T1 & T2 | 1T0 & 2T1 | 48.5 | 0 | n/a | n/a | 16.6814 | JELI 33kV
Stage 8: 48.5Hz | Kota Bharu | Tanah Merah | TMRH | 132 | Pasir Putih 1 & 2 | 305 & 405 | 48.5 | 0 | n/a | n/a | 83 | PPTH & SJTH
Stage 8: 48.5Hz | Kota Bharu | Kandis | KDIS | 132 | Pasir Putih 1 & 2 | 505 & 605 | 48.5 | 0 | n/a | n/a
Stage 9: 48.4Hz | Ayer Keroh | Kelemak | KLMK | 132 | CHNG & ZRNA | 305 & 805 | 48.4 | 0 | n/a | n/a | 268 | ZRNA, SPWR, CHNG, BMKA, MMKA, BVTA, MFDR, TGBU, PPSR, HLNM, BRBI
Stage 9: 48.4Hz | Ayer Keroh | Malim Jaya | MJYA | 132 | BVTA 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Ayer Keroh | Malacca | MCCA | 132 | BRBI 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Ayer Keroh | Malacca | MCCA | 132 | TGBU 1 & 2 | 905 & 1005 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Dungun | Kenyir Temporary | KNYT | 132 | KBRG & CHRG/KTGU | 305 & 205 | 48.4 | 0 | n/a | n/a | 153 | GBDK, KBRG, KTGU & BRKT | *GM to confirm the current relay installations post new KNYT configuration
Stage 9: 48.4Hz | Dungun | Chendering | CHRG | 132 | KBRG/KTGU & KNYT/KTGU | 205 & 305 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Kluang | Bukit Batu | BBTU | 132 | SNAI & SLNG | 205 & 505 | 48.4 | 0 | n/a | n/a | 232 | SLNG, SNAI, KLAI & UTMJ
Stage 9: 48.4Hz | Johor Bahru | Skudai | SDAI | 132 | SNAI & SLNG | 305 & 405 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Selangor | Batang Berjuntai | BTAI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 14.7682 | BTAI 33kV
Stage 9: 48.4Hz | Kuala Lumpur | K.L.East | KULE | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 61.6353 | KULE 33kV |  | 0.9 | 60 | 2
Stage 9: 48.4Hz | Kuala Lumpur | KL Pavilion | KLPV | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 68.7869 | KLPV 33kV
Stage 9: 48.4Hz | Perda | Tikam Batu | TKBU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 60.3016 | TKBU 33kV
Stage 10: 48.3Hz | Johor Bahru | Tampoi | TPOI | 22 | 132/22kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120 | 35.9347 | TPOI 22kV
Stage 10: 48.3Hz | Kluang | Batu Pahat East | BPHE | 132 | BPHT 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120 | 41 | BPHT, TPCH
Stage 10: 48.3Hz | Kluang | Yong Peng | YGPG | 132 | BPHT & TPCH | 105 & 205 | 48.3 | 0 | 49.3 | 120
Stage 10: 48.3Hz | Kluang | Yong Peng | YGPG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120 | - | YGPG 11kV
Stage 10: 48.3Hz | Selangor | Jalan Meru | MERU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.3 | 0 | 49.3 | 120 | 100.9312 | MERU 33 kV
Stage 10: 48.3Hz | Selangor | Proton | PROT | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120 | 115.4056 | PROT 33kV
Stage 10: 48.3Hz | Seremban | Kilat | KLAT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120 | 21.521 | KLAT 11kV
Stage 10: 48.3Hz | Alor Setar | Perlis Power Station | PLPS | 132 | TPAU | 705 | 48.3 | 0 | 49.3 | 120 | 96 | TPAU, TEWA, UMKA, KCMT
Stage 10: 48.3Hz | Alor Setar | Kuala Perlis | KPLS | 132 | TEWA 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120
Stage 10: 48.3Hz | Kuala Lumpur | Imbi | IMBI | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120 | 91.9517 | IMBI 33 kV |  | 0.9 | 60 | 2
Stage 10: 48.3Hz | Kuala Lumpur | Kota Damansara | KDSA | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120 | 148.4245 | KDSA 33kV
Stage 10: 48.3Hz | Kuala Lumpur | Galloway | GWAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.3 | 0 | 49.3 | 120 | 57.1456 | GWAY 33kV | Category 1: Reassignment of operating stage (Freq1: 48.2Hz --> 48.3Hz) and (Freq2: 49.3Hz @90s --> 49.3Hz @120)
Stage 10: 48.3Hz | Perda | Bukit Tambun | BTBN | 132 | VDOR/JNKO & NBTL Feeders | 105 & 205 | 48.3 | 0 | 49.3 | 120 | 144 | JNKO, VDOR, PBTR, NBTL | Category 2: New assignment (replacement for BMRH: BSRI 1 & 2 defeated due to LSS KNLS in the pocket load)
Stage 10: 48.3Hz | Perda | Bagan Serai | BSRI | 132 | PBTR & NBTL | 105 & 205 | 48.3 | 0 | 49.3 | 120
Stage 11: 48.2Hz | Perda | Sungai Pinang | SPNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90 | 80.5657 | SPNG 33kV
Stage 11: 48.2Hz | Seremban | Nilai | NLAI | 132 | MTIN & AMID | 505 & 605 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Seremban | Paroi | PROI | 132 | MTIN 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Kuala Lumpur | Kajang | KJNG | 132 | KEST 1 & 2 | 105 & 205 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Kuala Lumpur | National University | NUNI | 132 | BHGT 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Kuala Lumpur | Bukit Mahkamah | BMKM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90 | 51.7312 | BMKM 33kV
Stage 11: 48.2Hz | Johor Bahru | Tebrau | TBRU | 132 | PLGI 1 & 2 | 905 & 1005 | 48.2 | 0 | 49.3 | 90 | 152 | KTGI, UTRM, PUBB, PLGI | *GM to confirm the current relay installation (previous network configuration were UTRM & KTGI)
Stage 11: 48.2Hz | Johor Bahru | Pasak | PSAK | 132 | PUBB & KTGI | 505 & 605 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Kluang | Renggam | RNGM | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.2 | 0 | 49.3 | 90 | 7.3649 | RNGM 11kV
Stage 11: 48.2Hz | Kluang | Kluang | KLUG | 132 | KLID & NYOR | 105 & 205 | 48.2 | 0 | 49.3 | 90 | 111 | KLID, MSNG, TGMK & NYOR
Stage 12: 48.1Hz | Alor Setar | Kangar | KGAR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 33.8944 | KGAR 11kV
Stage 12: 48.1Hz | Ipoh | Sri Iskandar | SIKD | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 & 1W0 | 48.1 | 0 | 49.3 | 60 | 30.6965 | SIKD 33kV
Stage 12: 48.1Hz | Selangor | Ladang Kundang | LKDG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.1 | 0 | 49.3 | 60 | 36.7625 | LKDG 33kV
Stage 12: 48.1Hz | Selangor | Subang Jaya Town Centre | SJTC | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.1 | 0 | 49.3 | 60 | 54.0023 | SJTC 33kV
Stage 12: 48.1Hz | Perda | Bayan Baru | BBRU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60 | 98.3955 | BBRU 33kV
Stage 12: 48.1Hz | Seremban | Semarak | SMRK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 22.9899 | SMRK 11kV
Stage 12: 48.1Hz | Seremban | Semarak | SMRK | 132 | Hualon 1, 2 & 3 | 505605705 | 48.1 | 0 | 49.3 | 60 | 40 | HLNN
Stage 12: 48.1Hz | Johor Bahru | Seelong | SELG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 21.4779 | SELG 11kV
Stage 12: 48.1Hz | Johor Bahru | Stulang Darat | STUL | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60 | 22.8338 | STUL 22kV
Stage 12: 48.1Hz | Kluang | Batu Pahat East | BPHE | 132 | SGAD 1 & 2 | 105 & 205 | 48.1 | 0 | 49.3 | 60 | 105 | SGAD, PJML, PYSF, PSRI & SSLG
Stage 12: 48.1Hz | Ayer Keroh | Sungai Abong | SABG | 132 | PJML & PYSF | 305 & 405 | 48.1 | 0 | 49.3 | 60
UVLS Stage 1 | Kluang | Mersing | MSNG | 11 | 132/11kV T1 & T2 | 31 & 32 | n/a | n/a | n/a | n/a | 10 | MSNG 11kV |  | 0.9 | 30 | 1
UVLS Stage 1 | Johor Bahru | Saleng | SLNG | 11 | 132/11kV T1 & T2 | 31 & 32 | n/a | n/a | n/a | n/a | 22 | SLNG 11kV |  | 0.9 | 30 | 1
UVLS Stage 1 | Perda | Bukit Tengah | BTGH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 90 | BTGH 33kV |  | 0.9 | 30 | 1
UVLS Stage 2 | Kuala Lumpur | Batu Caves | BCVS | 11 | 132/11kV T1 & T2 | 31 & 32 | n/a | n/a | n/a | n/a | 16 | BCVS 11kV |  | 0.9 | 60 | 2
UVLS Stage 2 | Kuala Lumpur | Harta Kemuncak | HKCK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | n/a | n/a | n/a | n/a | 90 | HKCK 33kV |  | 0.9 | 60 | 2
UVLS Stage 2 | Johor Bahru | Saleng | SLNG | 33 | 132/33kV T3 &T4 | 3T0 & 4T0 | n/a | n/a | n/a | n/a | 22 | SLNG 33kV |  | 0.9 | 60 | 2
UVLS Stage 2 | Perda | Bukit Tambun | BTBN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 86 | BTBN 33kV |  | 0.9 | 60 | 2
UVLS Stage 3 | Kuala Lumpur | Harta Kemuncak | HKCK | 11 | 132/11kV T1 & T2 | 31 & 32 | n/a | n/a | n/a | n/a | 14 | HKCK 11kV |  | 0.9 | 90 | 3
UVLS Stage 3 | Kuala Lumpur | Taman Jaya | TJYA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 74 | TJYA 33kV |  | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Skudai | SDAI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 26 | SDAI 33kV |  | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Ulu Tiram | UTRM | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 22 | UTRM 22kV |  | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Ulu Tiram | UTRM | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | n/a | n/a | n/a | n/a | 64 | UTRM 33kV |  | 0.9 | 90 | 3
Statistic
Load Quantum By GM Office
Alor Setar | 250.0522 | 0
Ayer Keroh | 591.4514 | 0
Dungun | 215.6198 | 0
Ipoh | 441.2562 | 0
Johor Bahru | 588.7449 | 223.9789
Kluang | 963.4453 | 10
Kota Bharu | 310.159 | 0
Kuala Lumpur | 1961.1835 | 811.8014
Kuantan | 446.7296 | 0
Perda | 1426.5639 | 275.6068
Selangor | 2179.556 | 74.945
Seremban | 422.5179 | 0
By Region
Southern | 2143.6416 | 233.9789
Central | 4563.2574 | 886.7464
North | 2117.8723 | 275.6068
East | 972.5084 | 0
Load Quantum by Stage UFLS
Stage: Ride Through | 311
Stage 1: 49.2Hz | 1000.6459
Stage 2: 49.1Hz | 801.1582
Stage 3: 49.0Hz | 884.9727
Stage 4: 48.9Hz | 753.8154
Stage 5: 48.8Hz | 713.0498
Stage 6: 48.7Hz | 931.429
Stage 7: 48.6Hz | 906.0382
Stage 8: 48.5Hz | 915.6496
Stage 9: 48.4Hz | 858.492
Stage 10: 48.3Hz | 852.3143
Stage 11: 48.2Hz | 402.6618
Stage 12: 48.1Hz | 466.0528
Load Quantum by Stage UVLS
UVLS Stage 1 | 498.0355
UVLS Stage 2 | 470.2239
UVLS Stage 3 | 428.0727

## UFLS_review
UNDER-FREQUENCY LOAD SHEDDING (UFLS) | [14 empty] | UNDER-VOLTAGE LOAD SHEDDING (UVLS)
Assignment | GM - Subzone | Substation | Mnemonic | kV | Assigned Feeders | CB | Freq1 | Delay1 (s) | Freq2 | Delay2 (s) | MW Quantum 2024 | MW Quantum 2025 | Load Area Affected | UFLS 2024 Review Remarks | Voltage pickup setting (p.u) | Delay (s) | UVLS Operating Stage
Stage: Ride Through | Kuantan | Gebeng Industri | GBID | 132 | KSTL 1 & 2 | 105 & 405 | 49.3 | 0 | n/a | n/a | 0 |  | KSTL load
Stage: Ride Through | Johor Bahru | Tanjung Langsat | TLST | 132 | TLTP (Titan Petrochemicals) | 505 | 49.3 | 0 | n/a | n/a | 26 |  | TLTP
Stage: Ride Through | Johor Bahru | Pasir Gudang Darat | PGDT | 132 | TTAN 1 & 2 | 905 & 1005 | 49.3 | 0 | n/a | n/a | 28 |  | TTAN
Stage: Ride Through | Johor Bahru | Pasir Gudang Ind Est | PGIE | 132 | ASTM 1 & 2 | 805 & 905 | 49.3 | 0 | n/a | n/a | 2 |  | ASTM
Stage: Ride Through | Johor Bahru | Tanjung Langsat Industrial Estate | TLIE | 275 | BSTL 1 & 2 | L15 & L25 | 49.3 | 0 | n/a | n/a | 7 |  | BSTL
Stage: Ride Through | Kuantan | Tanjung Gelang | TGLN | 132 | JDSI 1 & 2 | 505 & 605 | 49.3 | 0 | n/a | n/a | 0 |  | JDSI
Stage: Ride Through | Dungun | Telok Kalong | TKLG | 275 | Perwaja 1 & 2 | L15 & L25 | 49.3 | 1 | n/a | n/a | 0 |  | PWSM
Stage: Ride Through | Selangor | Olak Lempit | OLPT | 275 | MGST 1 & 2 | L75 & L85 | 49.3 | 0 | n/a | n/a | 25 |  | MGST
Stage: Ride Through | Selangor | Bukit Raja GIS | BRGS | 132 | ASMB 1 & 2 | 11130, 11230, 11330 | 49.3 | 0 | n/a | n/a | 44 |  | ASMB
Stage: Ride Through | Selangor | Bukit Raja GIS | BRGS | 132 | MSWK | 7130, 7230 | 49.3 | 0 | n/a | n/a | 60 |  | MSWK
Stage: Ride Through | Perda | Bukit Tengah | BTGH | 132 | SRON 2 | 905 | 49.3 | 0 | n/a | n/a | 50 |  | SRON 905 only
Stage: Ride Through | Perda | Bedong | BDNG | 275 | PWGR 1 & 2 feeders | L35 & L45 | 49.3 | 0 | n/a | n/a | 6 |  | PWGR
Stage: Ride Through | Perda | Prai Industrial | PRID | 132 | SRON & SRNW | 505 & 605 | 49.3 | 0 | n/a | n/a | 17 |  | SRON & SRNW
Stage: Ride Through | Perda | SKS Prai | SKSP | 132 | MWTA 1 & 2 | 105 & 205 | 49.3 | 0 | n/a | n/a | 46 |  | MWTA
Stage 1: 49.2Hz | Johor Bahru | Cahaya Baru | CBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 21.3659 |  | CBRU 22kV
Stage 1: 49.2Hz | Johor Bahru | Pasir Gudang Darat | PGDT | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 21.8789 |  | PGDT 22kV
Stage 1: 49.2Hz | Johor Bahru | Tampoi Industries | TMPI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 64.0768 |  | TMPI 33kV
Stage 1: 49.2Hz | Perda | Sungai Ara (GIS) | SARA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 41.5461 |  | SARA 33kV
Stage 1: 49.2Hz | Kuantan | Pekan Industri AIP | PKNI | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a | 18.5562 |  | PKNI 33kV
Stage 1: 49.2Hz | Ayer Keroh | Hicom Pegoh | HPGH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 15.3861 |  | HPGH 33kV
Stage 1: 49.2Hz | Seremban | Enstek | ESTK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 36.4197 |  | ESTK 33kV
Stage 1: 49.2Hz | Seremban | Kg. Repah | KRPH | 11 | 132/11kV T1 & T2 | 30 & 32 | 49.2 | 0 | n/a | n/a | 20.2233 |  | KRPH 11kV
Stage 1: 49.2Hz | Ipoh | Pengkalan Industri | PKID | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a | 21.5372 |  | PKID 11kV
Stage 1: 49.2Hz | Ipoh | Pengkalan Industri | PKID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 25.2821 |  | PKID 33kV
Stage 1: 49.2Hz | Ipoh | Kinta Valley Resort | KVRT | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.2 | 0 | n/a | n/a | 61.5771 |  | KVRT 33 kV
Stage 1: 49.2Hz | Ipoh | Menglembu | MLBU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 83.9211 |  | MLBU 33kV
Stage 1: 49.2Hz | Selangor | Setia Alam | STIA | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a | 76.0234 |  | STIA 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Damansara City | DCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 28.4475 |  | DCTY 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Manjalara | MJLR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 89.8683 |  | MJLR 33kV |  | 0.9 | 30 | 1
Stage 1: 49.2Hz | Kuala Lumpur | Sri Hartamas | SHMS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 71.0055 |  | SHMS 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Suncity GIS | SCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T2 | 49.2 | 0 | n/a | n/a | 25.6995 |  | SCTY 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Cheras Jaya | CJYA | 33 | 132/33kV T1, T2 & T3 | 1T0 & 2T0 & 3T0 | 49.2 | 0 | n/a | n/a | 157.1371 |  | CJYA 33kV
Stage 1: 49.2Hz | Kuala Lumpur | Danau Desa | DDSA | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a | 60.7924 |  | DDSA 33kV
Stage 1: 49.2Hz | Alor Setar | Mergong | MGON | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a | 17.2107 |  | MGON 11kV
Stage 1: 49.2Hz | Alor Setar | Pauh | PAUH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a | 42.691 |  | PAUH 33kV
Stage 2: 49.1Hz | Ipoh | Temoh | TMOH | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.1 | 0 | n/a | n/a | 22.3732 |  | TMOH 33kV
Stage 2: 49.1Hz | Ipoh | Kelebang | KLBG | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.1 | 0 | n/a | n/a | 24.6724 |  | KLBG 33kV
Stage 2: 49.1Hz | Ipoh | New Khantan | NKAN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 32.1433 |  | NKAN 33kV
Stage 2: 49.1Hz | Ipoh | Tasik | TASK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 8.5343 |  | TASK 22kV
Stage 2: 49.1Hz | Kuala Lumpur | SPPK Cheras | SPKC | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 1W0 & 5T0 | 49.1 | 0 | n/a | n/a | 123.2475 |  | SPKC 33kV
Stage 2: 49.1Hz | Kuala Lumpur | National University | NUNI | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 24.5161 |  | NUNI 11kV
Stage 2: 49.1Hz | Johor Bahru | Plentong | PLTG | 230 | WA18 1 & 2 | H10 & H20 | 49.1 | 0 | n/a | n/a | - |  | TNB-Singapore Interconnection
Stage 2: 49.1Hz | Johor Bahru | Tebrau | TBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 29.3428 |  | TBRU 22kV
Stage 2: 49.1Hz | Kuantan | Kampung Awah | KAWA | 132 | KRYG 1 & 2 | 305 & 405 | 49.1 | 0 | n/a | n/a | 30 |  | KRYG
Stage 2: 49.1Hz | Seremban | Tuanku Jaafar (GIS) | TJGS | 132 | SHEL 1 & 2 | 505 & 605 | 49.1 | 0 | n/a | n/a | 36 |  | SHELL
Stage 2: 49.1Hz | Selangor | Hicom | HCOM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 77.918 |  | HCOM 33 kV
Stage 2: 49.1Hz | Selangor | Shah Alam East | SHAE | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 49.1 | 0 | n/a | n/a | 72.8698 |  | SHAE 33kV
Stage 2: 49.1Hz | Selangor | Shah Alam South | SHAS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 64 |  | SHAS 33kV
Stage 2: 49.1Hz | Kota Bharu | Panchor | PCOR | 33 | 132/33kV T2 & T3 & T4 | 2T0, 3T0 & 4T0 | 49.1 | 0 | n/a | n/a | 67.9031 |  | PCOR 33kV | Category 2: New assignment (to include 2T0)
Stage 2: 49.1Hz | Kluang | Johor Tengah | JTGH | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 20.2863 |  | JTGH 11kV
Stage 2: 49.1Hz | Perda | Seberang Jaya | SJAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a | 74.3213 |  | SJAY 33kV
Stage 2: 49.1Hz | Perda | Taman Intan | INTN | 33 | 132/33kV T3 & T4 | 3T0&4T0 | 49.1 | 0 | n/a | n/a | 51.9714 |  | INTN 33kV
Stage 2: 49.1Hz | Perda | Taman Intan | INTN | 11 | 132/11kV T1 & T2 | 31&32 | 49.1 | 0 | n/a | n/a | 31.6547 |  | INTN 22kV
Stage 2: 49.1Hz | Ayer Keroh | Malacca Power Station | MPSS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a | 9.404 |  | MPSS 11kV
Stage 3: 49.0Hz | Kota Bharu | Tunjang | TJUG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 60 |  | TJUG 33kV | Category 2: New assignment (replacement for TMRH: KKRI & MACG defeated due to LSS in the pocket load)
Stage 3: 49.0Hz | Ayer Keroh | Malim Jaya | MJYA | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 26.877 |  | MJYA 11kV
Stage 3: 49.0Hz | Ayer Keroh | Muar | MUAR | 11 | 132/11kV T2 & T3 | 32 & 33 | 49 | 0 | n/a | n/a | 32.3916 |  | MUAR 11kV
Stage 3: 49.0Hz | Selangor | Bukit Rajah | BRGS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 18.9852 |  | BRGS 11 kV
Stage 3: 49.0Hz | Selangor | Port Klang P/S | PKLG | 132 | IGBK 1 & 2 | 705 & 805 | 49 | 0 | n/a | n/a | 130 |  | IGBK & NKST
Stage 3: 49.0Hz | Selangor | Bukit Beruntung | BBTG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 41.8364 |  | BBTG 33kV
Stage 3: 49.0Hz | Kuantan | Bandar Indra Mahkota | BIMK | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 28.0406 |  | BIMK 11kV
Stage 3: 49.0Hz | Kuantan | Bandar Indra Mahkota | BIMK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 98.0819 |  | BIMK 33kV
Stage 3: 49.0Hz | Kuantan | Bentong | BNTG | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a | 23.208 |  | BNTG 11kV
Stage 3: 49.0Hz | Perda | Butterworth North | BWTN | 33 | 132/33 kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a |  |  | BWTN 33kV
Stage 3: 49.0Hz | Perda | Butterworth North | BWTN | 11 | 132/11kV T5 | 35 | 49 | 0 | n/a | n/a |  |  | BWTN 11kV
Stage 3: 49.0Hz | Perda | Prai GIS | PRGS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 61.6121 |  | PRGS 33 kV
Stage 3: 49.0Hz | Kuala Lumpur | Serdang Raya | SRDR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 85.1885 |  | SRDR 33kV
Stage 3: 49.0Hz | Kuala Lumpur | Ampang GIS | AMPG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 75.8672 |  | AMPG T3&T4
Stage 3: 49.0Hz | Kuala Lumpur | Air Hitam | AHTM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 65.0735 |  | AHTM 33kV
Stage 3: 49.0Hz | Kuala Lumpur | Bukit Jalil | BJLL | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a | 85.6804 |  | BJLL 33kV
Stage 3: 49.0Hz | Kuala Lumpur | Balakong | BLKG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a | 52.1303 |  | BLKG 33 kV
Stage 4: 48.9Hz | Kota Bharu | Kota Bharu | KBRU | 33 | 132/33kV T1 & T3 & T5 | 1T0 & 3T0 & 5T0 | 48.9 | 0 | n/a | n/a | 82.5745 |  | KBRU 33kV
Stage 4: 48.9Hz | Selangor | PJ Selatan | PJST | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 65.7207 |  | PJST 33 kV | Category 1: Reassignment of operating stage (Freq1: 48.8Hz --> 48.9Hz)
Stage 4: 48.9Hz | Kluang | Pasir Gudang Town Centre | PGTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 111.1269 |  | PGTC 33kV | Category 1: Reassignment of operating stage (Freq1: 49.2Hz --> 48.9Hz)
Stage 4: 48.9Hz | Johor Bahru | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 37.2708 |  | PGIE 22kV
Stage 4: 48.9Hz | Johor Bahru | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T3 | 3T0 | 48.9 | 0 | n/a | n/a | 15.0562 |  | PGIE 22kV
Stage 4: 48.9Hz | Selangor | Puchong Jaya | PCHJ | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 83.0514 |  | PCHJ 33kV
Stage 4: 48.9Hz | Selangor | New Subang Uda | NSDA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 62.5762 |  | NSDA 33 kV
Stage 4: 48.9Hz | Kuala Lumpur | Sri Damansara | SDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 67.9905 |  | SDAM 33kV | Category 1: Reassignment of the stage (Freq1: 49.0Hz --> 48.9Hz) | 0.9 | 60 | 2
Stage 4: 48.9Hz | Kuala Lumpur | New SEA Park | NSPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 68.1678 |  | NSPK 33 kV |  | 0.9 | 90 | 3
Stage 4: 48.9Hz | Kuala Lumpur | Serdang New | SRDN | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.9 | 0 | n/a | n/a | 51.941 |  | SRDN 33kV
Stage 4: 48.9Hz | Seremban | Sendayan | SDYN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a | 64.8369 |  | SDYN 33kV | Category 1: Reassignment of the stage (Freq1: 49.1Hz --> 48.9Hz)
Stage 4: 48.9Hz | Seremban | Lukut | LKUT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.9 | 0 | n/a | n/a | 17.6596 |  | LKUT 11kV
Stage 4: 48.9Hz | Kuantan | Tanjong Gelang | TGLN | 11 | 132/11kV T1 & T2 & T3 | 31 & 32 & 33 | 48.9 | 0 | n/a | n/a | 25.8429 |  | TGLN 11kV
Stage 5: 48.8Hz | Alor Setar | Kota Setar | KSTR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a | 25.7531 |  | KSTR 11kV
Stage 5: 48.8Hz | Kuala Lumpur | Kg Chempaka | KCPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 71.7948 |  | KCPK 33kV |  | 0.9 | 30 | 1
Stage 5: 48.8Hz | Selangor | New Rawang | NRWG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 74.945 |  | NRWG 33 kV |  | 0.9 | 90 | 3
Stage 5: 48.8Hz | Selangor | Bukit Kapar | BKPR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a | 69.4631 |  | BKPR 33kV
Stage 5: 48.8Hz | Selangor | Temasya | TMSY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 60.1524 |  | TMSY 33 kV
Stage 5: 48.8Hz | Ayer Keroh | Kelemak | KLMK | 132 | MTNH 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | 49 |  | TKMG, PPJG, MTNH
Stage 5: 48.8Hz | Seremban | Rantau | RTAU | 132 | TKMG 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a
Stage 5: 48.8Hz | Seremban | Paroi | PROI | 132 | TJID 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | 140 |  | TJID, TTJF, SSUN & STRA
Stage 5: 48.8Hz | Seremban | Rasah | RASA | 132 | Satria & TTJF | 505 & 605 | 48.8 | 0 | n/a | n/a
Stage 5: 48.8Hz | Kuantan | Bentong South | BNTS | 132 | BNTG & RBDR | 205 & 405 | 48.8 | 0 | n/a | n/a | 133 |  | BNTA, KLIP, JNKA, JTUT, RBDR | Category 2: New assignment - add JTUT 705
Stage 5: 48.8Hz | Kuantan | Kg. Awah | KAWA | 132 | JNKA & JTUT | 205 & 705 | 48.8 | 0 | n/a | n/a
Stage 5: 48.8Hz | Perda | Air terjun | ATJN | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a | 56.7503 |  | ATJN 33 kV
Stage 5: 48.8Hz | Perda | Gurun | GRUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a | 9.3912 |  | GRUN 11kV
Stage 5: 48.8Hz | Perda | Jeniang | JENG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a | 22.7999 |  | JENG 33kV
Stage 6: 48.7Hz | Ipoh | Lumut | LMUT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 58.1226 |  | LMUT 33kV
Stage 6: 48.7Hz | Ipoh | Lumut Maritime | LMTM | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 72.3964 |  | LMTM 33kV
Stage 6: 48.7Hz | Kuala Lumpur | Mutiara Damansara | MDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 38.9019 |  | MDAM 33kV
Stage 6: 48.7Hz | Kuala Lumpur | Batu Caves | BCVS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 84.9599 |  | BCVS 33kV |  | 0.9 | 90 | 3
Stage 6: 48.7Hz | Kluang | Parit Raja | PRJA | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 17.3238 |  | PRJA 11kV
Stage 6: 48.7Hz | Kluang | Yong Peng North | YGPN | 132 | CAAH & BSPT/BKPG | 105 & 205 | 48.7 | 0 | n/a | n/a | 298 |  | LKJG, XNSS, XNYI, TKID, TKAK, JMTH, SGMT, BSPT, BKPG, CAAH, BAHA, NSCI, GMAS, PBSR, KLPH, SPTG, KKWG | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Seremban | Paroi | PROI | 132 | KPLH 1 & 2 | 705 & 805 | 48.7 | 0 | n/a | n/a
Stage 6: 48.7Hz | Ayer Keroh | Lipat Kajang | LKJG | 132 | JSIN & MCOP | 505 & 605 | 48.7 | 0 | n/a | n/a
Stage 6: 48.7Hz | Ayer Keroh | Ujong Pasir | UPSR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 18 |  | UPSR 11kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Ayer Keroh | Ujong Pasir | UPSR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 60 |  | UPSR 33kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Ayer Keroh | Metacorp | MCOP | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 30 |  | MCOP 11kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Ayer Keroh | Metacorp | MCOP | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a | 61 |  | MCOP 33kV | Category 2: New assignment (replacement for UPSR: AKRH & AKRH/ONST defeated due to LSS JSLS in the pocket load)
Stage 6: 48.7Hz | Seremban | Nilai | NLAI | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 22.8675 |  | NLAI 11kV | Category 1: Reassignment of operating stage (Freq1: 48.9Hz --> 48.7Hz)
Stage 6: 48.7Hz | Selangor | Batu Tiga | BTGA | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.7 | 0 | n/a | n/a | 71.3972 |  | BTGA 33kV
Stage 6: 48.7Hz | Selangor | Bukit Badong | BBDG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a | 66.6988 |  | BBDG 33kV
Stage 6: 48.7Hz | Selangor | Rasa Selangor Industry | RSID | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a | 31.7609 |  | RSID 11kV
Stage 7: 48.6Hz | Ayer Keroh | Gerisik | GRSK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 21.3927 |  | GRSK 11kV
Stage 7: 48.6Hz | Johor Bahru | Kota Putri | KPTR | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 35.0813 |  | KPTR 22kV
Stage 7: 48.6Hz | Johor Bahru | Skudai | SDAI | 22 | 132/22kV T7 & T8 | 37 & 38 | 48.6 | 0 | n/a | n/a | 1.4469 |  | SDAI 22kV | Category 1: Reassignment of operating stage (Freq1: 48.2Hz --> 48.6Hz) and removing setting Freq2 (Freq2: 49.3Hz @ 90s --> n/a)
Stage 7: 48.6Hz | Johor Bahru | Larkin GIS | LKIN | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 33.3325 |  | LKIN 22kV |  | 0.9 | 30 | 1
Stage 7: 48.6Hz | Kuantan | Kg. Awah | KAWA | 132 | SONG | 605 | 48.6 | 0 | n/a | n/a | 90 |  | SONG, MTKB, TMID, MNID
Stage 7: 48.6Hz | Kuantan | Jambu Rias | JBRS | 132 | TMID | 205 | 48.6 | 0 | n/a | n/a
Stage 7: 48.6Hz | Perda | Gelugor | GLGR | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.6 | 0 | n/a | n/a | 61.1334 |  | GLGR 33kV
Stage 7: 48.6Hz | Perda | Bayan Mutiara | BMTR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 105.8642 |  | BMTR 33kV
Stage 7: 48.6Hz | Perda | Batu Kawan South | BTWS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 52.4377 |  | BTWS 33kV
Stage 7: 48.6Hz | Alor Setar | Kangar | KGAR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 14.2995 |  | KGAR 33kV
Stage 7: 48.6Hz | Selangor | Shah Alam West | SHAW | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 69.0504 |  | SHAW 33kV
Stage 7: 48.6Hz | Selangor | Shah Alam West | SHAW | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 15.0282 |  | SHAW 11kV
Stage 7: 48.6Hz | Selangor | Teluk Panglima Garang | TPGR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a | 98.751 |  | TPGR 33kV
Stage 7: 48.6Hz | Selangor | Shah Alam North | SHAN | 11 | 132/11kV T1, T2 & T3 | 31, 32 & 33 | 48.6 | 0 | n/a | n/a | 4.0549 |  | SHAN 11kV
Stage 7: 48.6Hz | Selangor | Shah Alam Section 18 GIS | SHLB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 77.1695 |  | SHLB 33kV | Category 1: Reassignment of operating stage (Freq1: 48.5Hz --> 48.6Hz)
Stage 7: 48.6Hz | Selangor | Bandar Botanic | BBTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 81.8867 |  | BBTC 33kV | Category 1: Reassignment removing setting for Freq2 (Freq2: 49.3Hz @ 120s --> n/a)
Stage 7: 48.6Hz | Perda | Bedong | BDNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 45.0985 |  | BDNG 33kV | Category 1: Reassignment of operating stage (Freq1: 48.7Hz --> 48.6Hz)
Stage 7: 48.6Hz | Kuala Lumpur | Kuala Lumpur North | KULN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a | 71.6655 |  | KULN 33kV
Stage 7: 48.6Hz | Dungun | Dungun | DGUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 9.9042 |  | DGUN 11kV
Stage 7: 48.6Hz | Dungun | Chendering | CHRG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a | 18.4411 |  | CHRG 11kV
Stage 8: 48.5Hz | Kluang | Kluang (New) | KLUG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 20.3434 |  | KLUG 11kV
Stage 8: 48.5Hz | Johor Bahru | Majidee | MAJD | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 34.6464 |  | MAJD 22kV |  | 0.9 | 60 | 2
Stage 8: 48.5Hz | Dungun | Dungun Industries | DGID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 17.7645 |  | DGID 33kV
Stage 8: 48.5Hz | Dungun | Chukai | CKAI | 33 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 16.51 |  | CKAI 11kV
Stage 8: 48.5Hz | Alor Setar | Tanjong Pauh | PAUH | 11 | 132/11kV T3 & T4 | 35 & 36 | 48.5 | 0 | n/a | n/a | 20.2035 |  | PAUH 11kV
Stage 8: 48.5Hz | Perda | Bukit Minyak | BMYK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a | 40.4944 |  | BMYK 11kV
Stage 8: 48.5Hz | Perda | Bukit Minyak | BMYK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 99.6068 |  | BMYK 33kV |  | 0.9 | 30 | 1
Stage 8: 48.5Hz | Perda | Prai Industries | PRID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 70.4984 |  | PRID 33kV
Stage 8: 48.5Hz | Perda | Prai Industries | PRID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 99.1207
Stage 8: 48.5Hz | Selangor | Puchong Perdana | PCHP | 33 | 132/33kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.5 | 0 | n/a | n/a | 96.6747 |  | PCHP 33kV
Stage 8: 48.5Hz | Selangor | Connaught Bridge PS | CBPS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a | 127.7547 |  | CBPS 33kV
Stage 8: 48.5Hz | Selangor | Bandar Baru Shah Alam | SHAB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 90.9176 |  | SHAB 33kV | Category 1: Reassignment of operating stage (Freq1: 48.4Hz --> 48.5Hz)
Stage 8: 48.5Hz | Kuala Lumpur | Segambut | SGBT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a | 81.4331 |  | SGBT 33kV |  | 0.9 | 30 | 1
Stage 8: 48.5Hz | Kota Bharu | Jeli | JELI | 33 | 275/33kV T1 & T2 | 1T0 & 2T1 | 48.5 | 0 | n/a | n/a | 16.6814 |  | JELI 33kV
Stage 8: 48.5Hz | Kota Bharu | Tanah Merah | TMRH | 132 | Pasir Putih 1 & 2 | 305 & 405 | 48.5 | 0 | n/a | n/a | 83 |  | PPTH & SJTH
Stage 8: 48.5Hz | Kota Bharu | Kandis | KDIS | 132 | Pasir Putih 1 & 2 | 505 & 605 | 48.5 | 0 | n/a | n/a
Stage 9: 48.4Hz | Ayer Keroh | Kelemak | KLMK | 132 | CHNG & ZRNA | 305 & 805 | 48.4 | 0 | n/a | n/a | 268 |  | ZRNA, SPWR, CHNG, BMKA, MMKA, BVTA, MFDR, TGBU, PPSR, HLNM, BRBI
Stage 9: 48.4Hz | Ayer Keroh | Malim Jaya | MJYA | 132 | BVTA 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Ayer Keroh | Malacca | MCCA | 132 | BRBI 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Ayer Keroh | Malacca | MCCA | 132 | TGBU 1 & 2 | 905 & 1005 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Dungun | Kenyir Temporary | KNYT | 132 | KBRG & CHRG/KTGU | 305 & 205 | 48.4 | 0 | n/a | n/a | 153 |  | GBDK, KBRG, KTGU & BRKT | *GM to confirm the current relay installations post new KNYT configuration
Stage 9: 48.4Hz | Dungun | Chendering | CHRG | 132 | KBRG/KTGU & KNYT/KTGU | 205 & 305 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Kluang | Bukit Batu | BBTU | 132 | SNAI & SLNG | 205 & 505 | 48.4 | 0 | n/a | n/a | 232 |  | SLNG, SNAI, KLAI & UTMJ
Stage 9: 48.4Hz | Johor Bahru | Skudai | SDAI | 132 | SNAI & SLNG | 305 & 405 | 48.4 | 0 | n/a | n/a
Stage 9: 48.4Hz | Selangor | Batang Berjuntai | BTAI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 14.7682 |  | BTAI 33kV
Stage 9: 48.4Hz | Kuala Lumpur | K.L.East | KULE | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 61.6353 |  | KULE 33kV |  | 0.9 | 60 | 2
Stage 9: 48.4Hz | Kuala Lumpur | KL Pavilion | KLPV | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 68.7869 |  | KLPV 33kV
Stage 9: 48.4Hz | Perda | Tikam Batu | TKBU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a | 60.3016 |  | TKBU 33kV
Stage 10: 48.3Hz | Johor Bahru | Tampoi | TPOI | 22 | 132/22kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120 | 35.9347 |  | TPOI 22kV
Stage 10: 48.3Hz | Kluang | Batu Pahat East | BPHE | 132 | BPHT 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120 | 41 |  | BPHT, TPCH
Stage 10: 48.3Hz | Kluang | Yong Peng | YGPG | 132 | BPHT & TPCH | 105 & 205 | 48.3 | 0 | 49.3 | 120
Stage 10: 48.3Hz | Kluang | Yong Peng | YGPG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120 | - |  | YGPG 11kV
Stage 10: 48.3Hz | Selangor | Jalan Meru | MERU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.3 | 0 | 49.3 | 120 | 100.9312 |  | MERU 33 kV
Stage 10: 48.3Hz | Selangor | Proton | PROT | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120 | 115.4056 |  | PROT 33kV
Stage 10: 48.3Hz | Seremban | Kilat | KLAT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120 | 21.521 |  | KLAT 11kV
Stage 10: 48.3Hz | Alor Setar | Perlis Power Station | PLPS | 132 | TPAU | 705 | 48.3 | 0 | 49.3 | 120 | 96 |  | TPAU, TEWA, UMKA, KCMT
Stage 10: 48.3Hz | Alor Setar | Kuala Perlis | KPLS | 132 | TEWA 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120
Stage 10: 48.3Hz | Kuala Lumpur | Imbi | IMBI | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120 | 91.9517 |  | IMBI 33 kV |  | 0.9 | 60 | 2
Stage 10: 48.3Hz | Kuala Lumpur | Kota Damansara | KDSA | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120 | 148.4245 |  | KDSA 33kV
Stage 10: 48.3Hz | Kuala Lumpur | Galloway | GWAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.3 | 0 | 49.3 | 120 | 57.1456 |  | GWAY 33kV | Category 1: Reassignment of operating stage (Freq1: 48.2Hz --> 48.3Hz) and (Freq2: 49.3Hz @90s --> 49.3Hz @120)
Stage 10: 48.3Hz | Perda | Bukit Tambun | BTBN | 132 | VDOR/JNKO & NBTL Feeders | 105 & 205 | 48.3 | 0 | 49.3 | 120 | 144 |  | JNKO, VDOR, PBTR, NBTL | Category 2: New assignment (replacement for BMRH: BSRI 1 & 2 defeated due to LSS KNLS in the pocket load)
Stage 10: 48.3Hz | Perda | Bagan Serai | BSRI | 132 | PBTR & NBTL | 105 & 205 | 48.3 | 0 | 49.3 | 120
Stage 11: 48.2Hz | Perda | Sungai Pinang | SPNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90 | 80.5657 |  | SPNG 33kV
Stage 11: 48.2Hz | Seremban | Nilai | NLAI | 132 | MTIN & AMID | 505 & 605 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Seremban | Paroi | PROI | 132 | MTIN 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Kuala Lumpur | Kajang | KJNG | 132 | KEST 1 & 2 | 105 & 205 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Kuala Lumpur | National University | NUNI | 132 | BHGT 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Kuala Lumpur | Bukit Mahkamah | BMKM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90 | 51.7312 |  | BMKM 33kV
Stage 11: 48.2Hz | Johor Bahru | Tebrau | TBRU | 132 | PLGI 1 & 2 | 905 & 1005 | 48.2 | 0 | 49.3 | 90 | 152 |  | KTGI, UTRM, PUBB, PLGI | *GM to confirm the current relay installation (previous network configuration were UTRM & KTGI)
Stage 11: 48.2Hz | Johor Bahru | Pasak | PSAK | 132 | PUBB & KTGI | 505 & 605 | 48.2 | 0 | 49.3 | 90
Stage 11: 48.2Hz | Kluang | Renggam | RNGM | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.2 | 0 | 49.3 | 90 | 7.3649 |  | RNGM 11kV
Stage 11: 48.2Hz | Kluang | Kluang | KLUG | 132 | KLID & NYOR | 105 & 205 | 48.2 | 0 | 49.3 | 90 | 111 |  | KLID, MSNG, TGMK & NYOR
Stage 12: 48.1Hz | Alor Setar | Kangar | KGAR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 33.8944 |  | KGAR 11kV
Stage 12: 48.1Hz | Ipoh | Sri Iskandar | SIKD | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 & 1W0 | 48.1 | 0 | 49.3 | 60 | 30.6965 |  | SIKD 33kV
Stage 12: 48.1Hz | Selangor | Ladang Kundang | LKDG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.1 | 0 | 49.3 | 60 | 36.7625 |  | LKDG 33kV
Stage 12: 48.1Hz | Selangor | Subang Jaya Town Centre | SJTC | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.1 | 0 | 49.3 | 60 | 54.0023 |  | SJTC 33kV
Stage 12: 48.1Hz | Perda | Bayan Baru | BBRU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60 | 98.3955 |  | BBRU 33kV
Stage 12: 48.1Hz | Seremban | Semarak | SMRK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 22.9899 |  | SMRK 11kV
Stage 12: 48.1Hz | Seremban | Semarak | SMRK | 132 | Hualon 1, 2 & 3 | 505605705 | 48.1 | 0 | 49.3 | 60 | 40 |  | HLNN
Stage 12: 48.1Hz | Johor Bahru | Seelong | SELG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 | 21.4779 |  | SELG 11kV
Stage 12: 48.1Hz | Johor Bahru | Stulang Darat | STUL | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60 | 22.8338 |  | STUL 22kV
Stage 12: 48.1Hz | Kluang | Batu Pahat East | BPHE | 132 | SGAD 1 & 2 | 105 & 205 | 48.1 | 0 | 49.3 | 60 | 105 |  | SGAD, PJML, PYSF, PSRI & SSLG
Stage 12: 48.1Hz | Ayer Keroh | Sungai Abong | SABG | 132 | PJML & PYSF | 305 & 405 | 48.1 | 0 | 49.3 | 60
UVLS Stage 1 | Kluang | Mersing | MSNG | 11 | 132/11kV T1 & T2 | 31 & 32 | n/a | n/a | n/a | n/a | 10 |  | MSNG 11kV |  | 0.9 | 30 | 1
UVLS Stage 1 | Johor Bahru | Saleng | SLNG | 11 | 132/11kV T1 & T2 | 31 & 32 | n/a | n/a | n/a | n/a | 22 |  | SLNG 11kV |  | 0.9 | 30 | 1
UVLS Stage 1 | Perda | Bukit Tengah | BTGH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 90 |  | BTGH 33kV |  | 0.9 | 30 | 1
UVLS Stage 2 | Kuala Lumpur | Batu Caves | BCVS | 11 | 132/11kV T1 & T2 | 31 & 32 | n/a | n/a | n/a | n/a | 16 |  | BCVS 11kV |  | 0.9 | 60 | 2
UVLS Stage 2 | Kuala Lumpur | Harta Kemuncak | HKCK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | n/a | n/a | n/a | n/a | 90 |  | HKCK 33kV |  | 0.9 | 60 | 2
UVLS Stage 2 | Johor Bahru | Saleng | SLNG | 33 | 132/33kV T3 &T4 | 3T0 & 4T0 | n/a | n/a | n/a | n/a | 22 |  | SLNG 33kV |  | 0.9 | 60 | 2
UVLS Stage 2 | Perda | Bukit Tambun | BTBN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 86 |  | BTBN 33kV |  | 0.9 | 60 | 2
UVLS Stage 3 | Kuala Lumpur | Harta Kemuncak | HKCK | 11 | 132/11kV T1 & T2 | 31 & 32 | n/a | n/a | n/a | n/a | 14 |  | HKCK 11kV |  | 0.9 | 90 | 3
UVLS Stage 3 | Kuala Lumpur | Taman Jaya | TJYA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 74 |  | TJYA 33kV |  | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Skudai | SDAI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 26 |  | SDAI 33kV |  | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Ulu Tiram | UTRM | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | n/a | n/a | n/a | n/a | 22 |  | UTRM 22kV |  | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Ulu Tiram | UTRM | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | n/a | n/a | n/a | n/a | 64 |  | UTRM 33kV |  | 0.9 | 90 | 3
Statistic
Load Quantum By GM Office
Alor Setar | 250.0522 | 0
Ayer Keroh | 591.4514 | 0
Dungun | 215.6198 | 0
Ipoh | 441.2562 | 0
Johor Bahru | 588.7449 | 223.9789
Kluang | 963.4453 | 10
Kota Bharu | 310.159 | 0
Kuala Lumpur | 1961.1835 | 811.8014
Kuantan | 446.7296 | 0
Perda | 1426.5639 | 275.6068
Selangor | 2179.556 | 74.945
Seremban | 422.5179 | 0
By Region
Southern | 2143.6416 | 233.9789
Central | 4563.2574 | 886.7464
North | 2117.8723 | 275.6068
East | 972.5084 | 0
Load Quantum by Stage UFLS
Stage: Ride Through | 311
Stage 1: 49.2Hz | 1000.6459
Stage 2: 49.1Hz | 801.1582
Stage 3: 49.0Hz | 884.9727
Stage 4: 48.9Hz | 753.8154
Stage 5: 48.8Hz | 713.0498
Stage 6: 48.7Hz | 931.429
Stage 7: 48.6Hz | 906.0382
Stage 8: 48.5Hz | 915.6496
Stage 9: 48.4Hz | 858.492
Stage 10: 48.3Hz | 852.3143
Stage 11: 48.2Hz | 402.6618
Stage 12: 48.1Hz | 466.0528
Load Quantum by Stage UVLS
UVLS Stage 1 | 498.0355
UVLS Stage 2 | 470.2239
UVLS Stage 3 | 428.0727

## TNB Load
Bus Number | Bus Name |  | Id | Zone Num | Zone Name | Owner Num | Owner Name | In Service | Pload (MW) | Qload (Mvar)
63177 | AYTH132 132.00 | AYTH | T7 | 1 | PERLIS | 1 | TNB T | 1 | 11.6897 | 4.0861
61123 | BKRS132 132.00 | BKRS | T1 | 1 | PERLIS | 1 | TNB T | 1 | 21.2899 | 0.2278
61123 | BKRS132 132.00 | BKRS | T2 | 1 | PERLIS | 1 | TNB T | 1 | 21.207 | 0.2278
51089 | CBJC132 132.00 | CBJC | T1 | 1 | PERLIS | 1 | TNB T | 1 | 27.6561 | -1.8784
96176 | CMBG132 132.00 | CMBG | T3 | 1 | PERLIS | 1 | TNB T | 1 | 18.4629 | 1.8432
61101 | CPNG132 132.00 | CPNG | T1 | 1 | PERLIS | 1 | TNB T | 1 | 5.7418 | 0.5561
61101 | CPNG132 132.00 | CPNG | T2 | 1 | PERLIS | 1 | TNB T | 1 | 5.7594 | 0.5612
61137 | KGAR132 132.00 | KGAR | T1 | 1 | PERLIS | 1 | TNB T | 1 | 12.0377 | 3.4565
61137 | KGAR132 132.00 | KGAR | T2 | 1 | PERLIS | 1 | TNB T | 1 | 11.7281 | 0.1325
61137 | KGAR132 132.00 | KGAR | T3 | 1 | PERLIS | 1 | TNB T | 1 | 7.408 | 0.1905
61137 | KGAR132 132.00 | KGAR | T4 | 1 | PERLIS | 1 | TNB T | 1 | 10.9504 | 0.3707
61102 | KPLS132 132.00 | KPLS | T1 | 1 | PERLIS | 1 | TNB T | 1 | 9.0347 | 1.1577
61102 | KPLS132 132.00 | KPLS | T2 | 1 | PERLIS | 1 | TNB T | 1 | 8.9167 | 1.1028
96116 | PMKA132 132.00 | PMKA | T1 | 1 | PERLIS | 1 | TNB T | 1 | 4.1555 | -0.0601
96116 | PMKA132 132.00 | PMKA | T2 | 1 | PERLIS | 1 | TNB T | 1 | 4.1555 | -0.059
61148 | AJYA132 132.00 | AJYA | T1 | 2 | KEDAH | 1 | TNB T | 1 | 0 | 0
61148 | AJYA132 132.00 | AJYA | T2 | 2 | KEDAH | 1 | TNB T | 1 | 16.3453 | 0.9319
61148 | AJYA132 132.00 | AJYA | T3 | 2 | KEDAH | 1 | TNB T | 1 | 20.0669 | -1.4973
61148 | AJYA132 132.00 | AJYA | T4 | 2 | KEDAH | 1 | TNB T | 1 | 0 | 0
61104 | ASTR132 132.00 | ASTR | T1 | 2 | KEDAH | 1 | TNB T | 1 | 5.9759 | 0.9692
61104 | ASTR132 132.00 | ASTR | T2 | 2 | KEDAH | 1 | TNB T | 1 | 5.8444 | 1.2788
61104 | ASTR132 132.00 | ASTR | T3 | 2 | KEDAH | 1 | TNB T | 1 | 26.3037 | 0.3676
61104 | ASTR132 132.00 | ASTR | T4 | 2 | KEDAH | 1 | TNB T | 1 | 12.719 | -6.6738
61115 | BDNG132 132.00 | BDNG | T1 | 2 | KEDAH | 1 | TNB T | 1 | 21.703 | 2.1155
61115 | BDNG132 132.00 | BDNG | T2 | 2 | KEDAH | 1 | TNB T | 1 | 18.7487 | 1.0821
61124 | BKHM132 132.00 | BKHM | T1 | 2 | KEDAH | 1 | TNB T | 1 | 6.0452 | 0.7932
61124 | BKHM132 132.00 | BKHM | T2 | 2 | KEDAH | 1 | TNB T | 1 | 6.0483 | 0.7932
61124 | BKHM132 132.00 | BKHM | T3 | 2 | KEDAH | 1 | TNB T | 1 | 18.2548 | -2.918
61124 | BKHM132 132.00 | BKHM | T4 | 2 | KEDAH | 1 | TNB T | 1 | 18.319 | -2.947
61120 | BSBU132 132.00 | BSBU | T1 | 2 | KEDAH | 1 | TNB T | 1 | 6.1395 | 0.6907
61120 | BSBU132 132.00 | BSBU | T2 | 2 | KEDAH | 1 | TNB T | 1 | 6.1125 | 0.6793
61120 | BSBU132 132.00 | BSBU | T3 | 2 | KEDAH | 1 | TNB T | 1 | 0 | 0
61120 | BSBU132 132.00 | BSBU | T4 | 2 | KEDAH | 1 | TNB T | 1 | 0 | 0
61108 | GCPD132 132.00 | GCPD | T1 | 2 | KEDAH | 1 | TNB T | 1 | 6.242 | 0.4339
61108 | GCPD132 132.00 | GCPD | T2 | 2 | KEDAH | 1 | TNB T | 1 | 6.2492 | 0.4318
61116 | GRNE132 132.00 | GRNE | T1 | 2 | KEDAH | 1 | TNB T | 1 | 16.9304 | -1.926
61116 | GRNE132 132.00 | GRNE | T2 | 2 | KEDAH | 1 | TNB T | 1 | 16.9325 | -1.9509
61109 | GRUN132 132.00 | GRUN | T1 | 2 | KEDAH | 1 | TNB T | 1 | 4.7177 | 0.1139
61109 | GRUN132 132.00 | GRUN | T2 | 2 | KEDAH | 1 | TNB T | 1 | 4.6991 | 0.1087
61131 | GTHR132 132.00 | GTHR | T1 | 2 | KEDAH | 1 | TNB T | 1 | 45.9937 | 9.1611
61131 | GTHR132 132.00 | GTHR | T2 | 2 | KEDAH | 1 | TNB T | 1 | 45.768 | 9.1196
61127 | INTN132 132.00 | INTN | T1 | 2 | KEDAH | 1 | TNB T | 1 | 16.5214 | 2.2926
61127 | INTN132 132.00 | INTN | T2 | 2 | KEDAH | 1 | TNB T | 1 | 15.0354 | 2.1652
61127 | INTN132 132.00 | INTN | T3 | 2 | KEDAH | 1 | TNB T | 1 | 25.3708 | 5.1112
61127 | INTN132 132.00 | INTN | T4 | 2 | KEDAH | 1 | TNB T | 1 | 24.5185 | 5.4674
61107 | JENG132 132.00 | JENG | T1 | 2 | KEDAH | 1 | TNB T | 1 | 14.4773 | 2.1642
61107 | JENG132 132.00 | JENG | T2 | 2 | KEDAH | 1 | TNB T | 1 | 13.914 | -3.4927
61141 | KERC132 132.00 | KERC | T1 | 2 | KEDAH | 1 | TNB T | 1 | 0 | 0
61141 | KERC132 132.00 | KERC | T2 | 2 | KEDAH | 1 | TNB T | 1 | 0 | 0
61122 | KKTL132 132.00 | KKTL | T1 | 2 | KEDAH | 1 | TNB T | 1 | 2.9998 | 0.3345
61122 | KKTL132 132.00 | KKTL | T2 | 2 | KEDAH | 1 | TNB T | 1 | 6.8405 | 2.1632
61122 | KKTL132 132.00 | KKTL | T3 | 2 | KEDAH | 1 | TNB T | 1 | 20.566 | 1.1225
61122 | KKTL132 132.00 | KKTL | T4 | 2 | KEDAH | 1 | TNB T | 1 | 20.7876 | 1.1018
61113 | KLIM132 132.00 | KLIM | T1 | 2 | KEDAH | 1 | TNB T | 1 | 34.6395 | 5.6963
61113 | KLIM132 132.00 | KLIM | T2 | 2 | KEDAH | 1 | TNB T | 1 | 34.8683 | 5.7201
61135 | KSSM132 132.00 | KSSM | T1 | 2 | KEDAH | 1 | TNB T | 1 | 5.3318 | 0.0321
61135 | KSSM132 132.00 | KSSM | T2 | 2 | KEDAH | 1 | TNB T | 1 | 5.3515 | 0.0259
61135 | KSSM132 132.00 | KSSM | T3 | 2 | KEDAH | 1 | TNB T | 1 | 12.456 | -0.1543
61135 | KSSM132 132.00 | KSSM | T4 | 2 | KEDAH | 1 | TNB T | 1 | 12.5658 | -0.1791
561111 | KSTR132R 132.00 | KSTR | T8 | 2 | KEDAH | 1 | TNB T | 1 | 26.6486 | 3.0081
161111 | KSTR_T 132.00 | KSTR | T7 | 2 | KEDAH | 1 | TNB T | 1 | 36.2766 | 6.505
61119 | MGON132 132.00 | MGON | T1 | 2 | KEDAH | 1 | TNB T | 1 | 8.2591 | 1.0075
61119 | MGON132 132.00 | MGON | T2 | 2 | KEDAH | 1 | TNB T | 1 | 8.2529 | 0.9941
61119 | MGON132 132.00 | MGON | T3 | 2 | KEDAH | 1 | TNB T | 1 | 49.2349 | 3.5766
61119 | MGON132 132.00 | MGON | T4 | 2 | KEDAH | 1 | TNB T | 1 | 45.9689 | 4.93
61132 | PAUH132 132.00 | PAUH | T1 | 2 | KEDAH | 1 | TNB T | 1 | 18.8088 | 0.1522
61132 | PAUH132 132.00 | PAUH | T2 | 2 | KEDAH | 1 | TNB T | 1 | 18.9869 | 0.1357
61132 | PAUH132 132.00 | PAUH | T3 | 2 | KEDAH | 1 | TNB T | 1 | 10.7723 | -1.5833
61132 | PAUH132 132.00 | PAUH | T4 | 2 | KEDAH | 1 | TNB T | 1 | 10.8261 | -1.605
61132 | PAUH132 132.00 | PAUH | T5 | 2 | KEDAH | 1 | TNB T | 1 | 11.9787 | -2.2771
61106 | SPID132 132.00 | SPID | T1 | 2 | KEDAH | 1 | TNB T | 1 | 9.7471 | -0.0518
61106 | SPID132 132.00 | SPID | T2 | 2 | KEDAH | 1 | TNB T | 1 | 10.0816 | 3.9473
61106 | SPID132 132.00 | SPID | T3 | 2 | KEDAH | 1 | TNB T | 1 | 43.6566 | 4.5034
61106 | SPID132 132.00 | SPID | T4 | 2 | KEDAH | 1 | TNB T | 1 | 43.9507 | 4.5852
61112 | TKBU132 132.00 | TKBU | T1 | 2 | KEDAH | 1 | TNB T | 1 | 31.6376 | 0.7973
61112 | TKBU132 132.00 | TKBU | T2 | 2 | KEDAH | 1 | TNB T | 1 | 31.707 | 0.7953
62105 | ATJN132 132.00 | ATJN | T1 | 3 | P PINANG | 1 | TNB T | 1 | 5.3577 | 0.4318
62105 | ATJN132 132.00 | ATJN | T2 | 3 | P PINANG | 1 | TNB T | 1 | 9.6001 | 0.9806
62105 | ATJN132 132.00 | ATJN | T3 | 3 | P PINANG | 1 | TNB T | 1 | 22.4579 | 0.4059
62105 | ATJN132 132.00 | ATJN | T4 | 3 | P PINANG | 1 | TNB T | 1 | 23.0864 | -2.5028
62131 | BBRU132 132.00 | BBRU | T1 | 3 | P PINANG | 41 | REACTORS | 1 | 48.453 | 10.7236
62131 | BBRU132 132.00 | BBRU | T2 | 3 | P PINANG | 41 | REACTORS | 1 | 48.1662 | 10.6408
62131 | BBRU132 132.00 | BBRU | T3 | 3 | P PINANG | 41 | REACTORS | 1 | 5.367 | 1.0759
62131 | BBRU132 132.00 | BBRU | T4 | 3 | P PINANG | 41 | REACTORS | 1 | 11.4205 | 2.5753
562131 | BBRU132NEW 132.00 | BBRU | T2 | 3 | P PINANG | 41 | REACTORS | 1 | 41.7733 | 10.6722
562131 | BBRU132NEW 132.00 | BBRU | T4 | 3 | P PINANG | 41 | REACTORS | 1 | 12.6684 | 3.6028
562131 | BBRU132NEW 132.00 | BBRU | T8 | 3 | P PINANG | 41 | REACTORS | 1 | 14.1979 | 5.8937
62120 | BKWS132 132.00 | BKWS | T1 | 3 | P PINANG | 1 | TNB T | 1 | 55.8776 | 15.1897
62120 | BKWS132 132.00 | BKWS | T2 | 3 | P PINANG | 1 | TNB T | 1 | 54.3657 | 3.4099
62120 | BKWS132 132.00 | BKWS | T5 | 3 | P PINANG | 1 | TNB T | 1 | 1.0262 | 0.0967
61117 | BLIN132 132.00 | BLIN | T1 | 3 | P PINANG | 1 | TNB T | 1 | 15.6174 | 1.516
61117 | BLIN132 132.00 | BLIN | T2 | 3 | P PINANG | 1 | TNB T | 1 | 14.2102 | -2.6592
62102 | BLPS132L 132.00 | BLPS | T3 | 3 | P PINANG | 1 | TNB T | 1 | 43.2683 | 7.8356
62102 | BLPS132L 132.00 | BLPS | T4 | 3 | P PINANG | 1 | TNB T | 1 | 46.5798 | 7.4432
62104 | BLPS132R 132.00 | BLPS | T1 | 3 | P PINANG | 1 | TNB T | 1 | 36.0571 | 7.2941
62104 | BLPS132R 132.00 | BLPS | T2 | 3 | P PINANG | 1 | TNB T | 1 | 35.3115 | 6.9047
62106 | BMJM132 132.00 | BMJM | T1 | 3 | P PINANG | 1 | TNB T | 1 | 9.5618 | 0.993
62106 | BMJM132 132.00 | BMJM | T2 | 3 | P PINANG | 1 | TNB T | 1 | 12.9313 | 1.2768
62106 | BMJM132 132.00 | BMJM | T3 | 3 | P PINANG | 1 | TNB T | 1 | 21.293 | 2.3485
62106 | BMJM132 132.00 | BMJM | T4 | 3 | P PINANG | 1 | TNB T | 1 | 21.2712 | 2.3713
62110 | BMTR132 132.00 | BMTR | T1 | 3 | P PINANG | 1 | TNB T | 1 | 62.7419 | 30.1113
62110 | BMTR132 132.00 | BMTR | T2 | 3 | P PINANG | 1 | TNB T | 1 | 57.494 | -4.8969
62108 | BMYK132 132.00 | BMYK | T1 | 3 | P PINANG | 1 | TNB T | 1 | 11.9517 | 2.6478
62108 | BMYK132 132.00 | BMYK | T2 | 3 | P PINANG | 1 | TNB T | 1 | 14.6306 | 3.6025
62108 | BMYK132 132.00 | BMYK | T3 | 3 | P PINANG | 1 | TNB T | 1 | 49.2069 | 8.1494
62108 | BMYK132 132.00 | BMYK | T4 | 3 | P PINANG | 1 | TNB T | 1 | 48.2977 | 8.0241
62101 | BTBN132 132.00 | BTBN | T1 | 3 | P PINANG | 1 | TNB T | 1 | 40.3296 | 4.551
62101 | BTBN132 132.00 | BTBN | T2 | 3 | P PINANG | 1 | TNB T | 1 | 40.7624 | 4.5945
462114 | BTGH132NEW 132.00 | BTGH | T1 | 3 | P PINANG | 1 | TNB T | 1 | 49.9835 | 9.247
462114 | BTGH132NEW 132.00 | BTGH | T2 | 3 | P PINANG | 1 | TNB T | 1 | 47.0033 | 9.0596
62133 | BWTN132 132.00 | BWTN | T1 | 3 | P PINANG | 1 | TNB T | 1 | 38.7007 | 2.7834
62133 | BWTN132 132.00 | BWTN | T2 | 3 | P PINANG | 1 | TNB T | 1 | 39.9982 | 2.8652
62133 | BWTN132 132.00 | BWTN | T5 | 3 | P PINANG | 1 | TNB T | 1 | 0 | 0
62109 | DKMT132 132.00 | DKMT | T1 | 3 | P PINANG | 1 | TNB T | 1 | 8.9374 | 0.438
62109 | DKMT132 132.00 | DKMT | T2 | 3 | P PINANG | 1 | TNB T | 1 | 8.9964 | 0.437
61163 | EVEM132 132.00 | EVEM | T1 | 3 | P PINANG | 1 | TNB T | 1 | 1.1542 | 0.1732
61163 | EVEM132 132.00 | EVEM | T2 | 3 | P PINANG | 1 | TNB T | 1 | 3.5837 | 0.9222
62103 | FLIM132 132.00 | FLIM | T1 | 3 | P PINANG | 1 | TNB T | 1 | 11.464 | 1.2312
62103 | FLIM132 132.00 | FLIM | T2 | 3 | P PINANG | 1 | TNB T | 1 | 5.8651 | 0.5913
62103 | FLIM132 132.00 | FLIM | T3 | 3 | P PINANG | 1 | TNB T | 1 | 26.7438 | 0.9527
62103 | FLIM132 132.00 | FLIM | T4 | 3 | P PINANG | 1 | TNB T | 1 | 23.2676 | 1.4041
62118 | GLGR132 132.00 | GLGR | T1 | 3 | P PINANG | 1 | TNB T | 1 | 19.1961 | -4.6577
62118 | GLGR132 132.00 | GLGR | T2 | 3 | P PINANG | 1 | TNB T | 1 | 21.3737 | 0.8677
62118 | GLGR132 132.00 | GLGR | T3 | 3 | P PINANG | 1 | TNB T | 1 | 21.4069 | 0.8812
62221 | ITLM275 275.00 | ITLM | F1 | 3 | P PINANG | 1 | TNB T | 1 | 0 | 0
62221 | ITLM275 275.00 | ITLM | F2 | 3 | P PINANG | 1 | TNB T | 1 | 0 | 0
62111 | NTBL132 132.00 | NTBL | T1 | 3 | P PINANG | 1 | TNB T | 1 | 11.9238 | 1.8349
62111 | NTBL132 132.00 | NTBL | T2 | 3 | P PINANG | 1 | TNB T | 1 | 14.8252 | 2.2553
62137 | PRGS132 132.00 | PRGS | T1 | 3 | P PINANG | 1 | TNB T | 1 | 12.5585 | 2.5059
62137 | PRGS132 132.00 | PRGS | T2 | 3 | P PINANG | 1 | TNB T | 1 | 7.584 | 1.634
562137 | PRGS132R 132.00 | PRGS | T3 | 3 | P PINANG | 1 | TNB T | 1 | 21.0455 | -3.8427
562137 | PRGS132R 132.00 | PRGS | T4 | 3 | P PINANG | 1 | TNB T | 1 | 21.0061 | -3.9287
62155 | PRID132 132.00 | PRID | T1 | 3 | P PINANG | 1 | TNB T | 1 | 23.6135 | 4.3398
62155 | PRID132 132.00 | PRID | T2 | 3 | P PINANG | 1 | TNB T | 1 | 23.4313 | 4.2859
62155 | PRID132 132.00 | PRID | T3 | 3 | P PINANG | 1 | TNB T | 1 | 36.8203 | 7.1967
62155 | PRID132 132.00 | PRID | T4 | 3 | P PINANG | 1 | TNB T | 1 | 36.9093 | 7.2961
62128 | SARA132 132.00 | SARA | T1 | 3 | P PINANG | 1 | TNB T | 1 | 35.6077 | 1.5211
62128 | SARA132 132.00 | SARA | T2 | 3 | P PINANG | 1 | TNB T | 1 | 35.7174 | 1.5211
62112 | SJAY132 132.00 | SJAY | T1 | 3 | P PINANG | 1 | TNB T | 1 | 42.5776 | 6.1239
62112 | SJAY132 132.00 | SJAY | T2 | 3 | P PINANG | 1 | TNB T | 1 | 42.9918 | 6.1964
62107 | SKCL132 132.00 | SKCL | T1 | 3 | P PINANG | 1 | TNB T | 1 | 11.552 | 1.3275
62107 | SKCL132 132.00 | SKCL | T2 | 3 | P PINANG | 1 | TNB T | 1 | 9.2791 | 0.8905
62107 | SKCL132 132.00 | SKCL | T3 | 3 | P PINANG | 1 | TNB T | 1 | 22.3989 | -4.4174
62107 | SKCL132 132.00 | SKCL | T4 | 3 | P PINANG | 1 | TNB T | 1 | 22.9208 | 8.1514
62124 | SPAE132 132.00 | SPAE | T1 | 3 | P PINANG | 1 | TNB T | 1 | 36.4433 | 3.996
62124 | SPAE132 132.00 | SPAE | T2 | 3 | P PINANG | 1 | TNB T | 1 | 36.0654 | 3.9566
62117 | SPG4132 132.00 | SPG4 | T1 | 3 | P PINANG | 1 | TNB T | 1 | 0 | 0
562117 | SPG4132R 132.00 | SPG4 | T2 | 3 | P PINANG | 1 | TNB T | 1 | 0 | 0
62135 | SPNG132 132.00 | SPNG | T1 | 3 | P PINANG | 1 | TNB T | 1 | 27.4583 | 3.5766
62135 | SPNG132 132.00 | SPNG | T2 | 3 | P PINANG | 1 | TNB T | 1 | 25.9372 | 2.7078
62125 | TGLR132 132.00 | TGLR | T1 | 3 | P PINANG | 1 | TNB T | 1 | 20.4977 | 1.3824
62125 | TGLR132 132.00 | TGLR | T2 | 3 | P PINANG | 1 | TNB T | 1 | 20.6364 | 1.2032
62127 | TGTK132 132.00 | TGTK | T1 | 3 | P PINANG | 1 | TNB T | 1 | 21.5425 | 2.8331
62127 | TGTK132 132.00 | TGTK | T2 | 3 | P PINANG | 1 | TNB T | 1 | 21.7807 | 2.8828
62122 | VDOR132 132.00 | VDOR | T1 | 3 | P PINANG | 1 | TNB T | 1 | 12.69 | 0.5064
62122 | VDOR132 132.00 | VDOR | T2 | 3 | P PINANG | 1 | TNB T | 1 | 15.5097 | 3.1552
62122 | VDOR132 132.00 | VDOR | T7 | 3 | P PINANG | 1 | TNB T | 1 | 14.6066 | -1.956
562122 | VDOR_T7 132.00 | VDOR | T7 | 3 | P PINANG | 1 | TNB T | 1 | 0 | 0
63106 | BDOR132 132.00 | BDOR | T1 | 4 | PERAK | 1 | TNB T | 1 | 13.738 | 1.6319
63106 | BDOR132 132.00 | BDOR | T2 | 4 | PERAK | 1 | TNB T | 1 | 6.7867 | 0.8356
63106 | BDOR132 132.00 | BDOR | T3 | 4 | PERAK | 1 | TNB T | 1 | 15.8017 | -2.8031
63106 | BDOR132 132.00 | BDOR | T4 | 4 | PERAK | 1 | TNB T | 1 | 15.7965 | -2.7617
63153 | BMRH132 132.00 | BMRH | T3 | 4 | PERAK | 1 | TNB T | 1 | 11.9486 | -3.4813
63153 | BMRH132 132.00 | BMRH | T4 | 4 | PERAK | 1 | TNB T | 1 | 11.9787 | -3.4461
63151 | BSRI132 132.00 | BSRI | T1 | 4 | PERAK | 1 | TNB T | 1 | 6.388 | 0.5312
63151 | BSRI132 132.00 | BSRI | T2 | 4 | PERAK | 1 | TNB T | 1 | 15.8276 | 1.2022
63166 | BTNG132 132.00 | BTNG | T1 | 4 | PERAK | 1 | TNB T | 1 | 14.1656 | -0.0518
63166 | BTNG132 132.00 | BTNG | T2 | 4 | PERAK | 1 | TNB T | 1 | 14.3106 | -0.0621
63141 | CEND132 132.00 | CEND | T1 | 4 | PERAK | 1 | TNB T | 1 | 8.6226 | -0.8854
63141 | CEND132 132.00 | CEND | T2 | 4 | PERAK | 1 | TNB T | 1 | 8.604 | -0.8998
63124 | GPRD132 132.00 | GPRD | T1 | 4 | PERAK | 1 | TNB T | 1 | 5.5316 | 1.05
63124 | GPRD132 132.00 | GPRD | T2 | 4 | PERAK | 1 | TNB T | 1 | 10.5393 | 1.4528
63124 | GPRD132 132.00 | GPRD | T3 | 4 | PERAK | 1 | TNB T | 1 | 51.2168 | 7.262
63124 | GPRD132 132.00 | GPRD | T4 | 4 | PERAK | 1 | TNB T | 1 | 50.7798 | 7.1915
63209 | GRIK275 275.00 | GRIK | T1 | 4 | PERAK | 41 | REACTORS | 1 | 9.6871 | 53.7051
63176 | GTWN132 132.00 | GTWN | T1 | 4 | PERAK | 1 | TNB T | 1 | 12.7636 | 2.0379
63176 | GTWN132 132.00 | GTWN | T2 | 4 | PERAK | 1 | TNB T | 1 | 11.9289 | 2.1777
63136 | HMLG132 132.00 | HMLG | T1 | 4 | PERAK | 1 | TNB T | 1 | 32.5053 | 3.1075
63136 | HMLG132 132.00 | HMLG | T2 | 4 | PERAK | 1 | TNB T | 1 | 32.3925 | 3.1189
63128 | KGJH132 132.00 | KGJH | T1 | 4 | PERAK | 1 | TNB T | 1 | 9.1642 | -1.9467
63128 | KGJH132 132.00 | KGJH | T2 | 4 | PERAK | 1 | TNB T | 1 | 8.3668 | -1.6464
63148 | KJWA132 132.00 | KJWA | T1 | 4 | PERAK | 1 | TNB T | 1 | 7.3168 | 1.487
63148 | KJWA132 132.00 | KJWA | T2 | 4 | PERAK | 1 | TNB T | 1 | 6.6272 | 1.691
63138 | KKSR132 132.00 | KKSR | T1 | 4 | PERAK | 1 | TNB T | 1 | 11.696 | 1.0707
63138 | KKSR132 132.00 | KKSR | T2 | 4 | PERAK | 1 | TNB T | 1 | 8.2239 | 1.3254
63155 | KLBG132 132.00 | KLBG | T1 | 4 | PERAK | 1 | TNB T | 1 | 15.3295 | 2.0845
63155 | KLBG132 132.00 | KLBG | T2 | 4 | PERAK | 1 | TNB T | 1 | 15.1918 | 2.0886
63155 | KLBG132 132.00 | KLBG | T3 | 4 | PERAK | 1 | TNB T | 1 | 11.2807 | -2.3226
63155 | KLBG132 132.00 | KLBG | T4 | 4 | PERAK | 1 | TNB T | 1 | 11.2352 | -2.2512
63104 | KMPR132 132.00 | KMPR | T1 | 4 | PERAK | 1 | TNB T | 1 | 0 | 0
63104 | KMPR132 132.00 | KMPR | T2 | 4 | PERAK | 1 | TNB T | 1 | 24.0919 | 2.4904
63104 | KMPR132 132.00 | KMPR | T3 | 4 | PERAK | 1 | TNB T | 1 | 15.3005 | 0.1232
63104 | KMPR132 132.00 | KMPR | T4 | 4 | PERAK | 1 | TNB T | 1 | 15.5056 | 0.0611
63119 | KMTG132 132.00 | KMTG | T1 | 4 | PERAK | 1 | TNB T | 1 | 10.0278 | 1.3938
63119 | KMTG132 132.00 | KMTG | T2 | 4 | PERAK | 1 | TNB T | 1 | 10.0702 | 1.3886
63119 | KMTG132 132.00 | KMTG | T3 | 4 | PERAK | 1 | TNB T | 1 | 6.5547 | 0.8222
63119 | KMTG132 132.00 | KMTG | T4 | 4 | PERAK | 1 | TNB T | 1 | 8.4807 | 1.4207
63173 | KVRT132 132.00 | KVRT | T1 | 4 | PERAK | 1 | TNB T | 1 | 12.8485 | 1.7334
63173 | KVRT132 132.00 | KVRT | T2 | 4 | PERAK | 1 | TNB T | 1 | 10.9721 | 0.8481
63173 | KVRT132 132.00 | KVRT | T3 | 4 | PERAK | 1 | TNB T | 1 | 33.9395 | 5.6279
63173 | KVRT132 132.00 | KVRT | T4 | 4 | PERAK | 1 | TNB T | 1 | 33.9333 | 5.6435
63131 | LMTM132 132.00 | LMTM | T1 | 4 | PERAK | 1 | TNB T | 1 | 12.4063 | 2.014
63131 | LMTM132 132.00 | LMTM | T2 | 4 | PERAK | 1 | TNB T | 1 | 12.3649 | 2.0078
63131 | LMTM132 132.00 | LMTM | T3 | 4 | PERAK | 1 | TNB T | 1 | 41.5587 | 3.3374
63131 | LMTM132 132.00 | LMTM | T4 | 4 | PERAK | 1 | TNB T | 1 | 39.8843 | 3.9991
63129 | LMUT132 132.00 | LMUT | T1 | 4 | PERAK | 1 | TNB T | 1 | 42.3395 | 3.4109
63129 | LMUT132 132.00 | LMUT | T2 | 4 | PERAK | 1 | TNB T | 1 | 43.2455 | 4.4371
63129 | LMUT132 132.00 | LMUT | T3 | 4 | PERAK | 40 | CAPACITORS | 1 | 27.7783 | 2.8186
63160 | MERY132 132.00 | MERY | T1 | 4 | PERAK | 1 | TNB T | 1 | 3.6346 | -0.2175
63160 | MERY132 132.00 | MERY | T2 | 4 | PERAK | 1 | TNB T | 1 | 3.6139 | -0.2382
63146 | MLBU132 132.00 | MLBU | T1 | 4 | PERAK | 1 | TNB T | 1 | 8.4952 | 1.1929
63146 | MLBU132 132.00 | MLBU | T2 | 4 | PERAK | 1 | TNB T | 1 | 12.5813 | 1.7148
63146 | MLBU132 132.00 | MLBU | T3 | 4 | PERAK | 1 | TNB T | 1 | 34.4842 | 5.8154
63146 | MLBU132 132.00 | MLBU | T4 | 4 | PERAK | 1 | TNB T | 1 | 34.6333 | 5.8557
63142 | NKAN132 132.00 | NKAN | T1 | 4 | PERAK | 1 | TNB T | 1 | 14.7455 | 2.1538
63142 | NKAN132 132.00 | NKAN | T2 | 4 | PERAK | 1 | TNB T | 1 | 14.8076 | 2.1642
63118 | PBTR132 132.00 | PBTR | T1 | 4 | PERAK | 1 | TNB T | 1 | 19.1557 | 3.0247
63118 | PBTR132 132.00 | PBTR | T2 | 4 | PERAK | 1 | TNB T | 1 | 22.1845 | 4.1026
63120 | PKCB132 132.00 | PKCB | T1 | 4 | PERAK | 1 | TNB T | 1 | 2.4552 | 0.2817
63120 | PKCB132 132.00 | PKCB | T2 | 4 | PERAK | 1 | TNB T | 1 | 2.4179 | 0.0435
63145 | PKID132 132.00 | PKID | T1 | 4 | PERAK | 1 | TNB T | 1 | 5.4146 | 0.6534
63145 | PKID132 132.00 | PKID | T2 | 4 | PERAK | 1 | TNB T | 1 | 9.6612 | 1.428
63145 | PKID132 132.00 | PKID | T3 | 4 | PERAK | 1 | TNB T | 1 | 12.6652 | -1.3047
63145 | PKID132 132.00 | PKID | T4 | 4 | PERAK | 1 | TNB T | 1 | 12.6579 | -1.2374
63133 | PKLN132 132.00 | PKLN | T1 | 4 | PERAK | 1 | TNB T | 1 | 6.7546 | 0.6876
63133 | PKLN132 132.00 | PKLN | T2 | 4 | PERAK | 1 | TNB T | 1 | 16.7699 | 2.9522
63133 | PKLN132 132.00 | PKLN | T3 | 4 | PERAK | 1 | TNB T | 1 | 35.4928 | 2.45
63133 | PKLN132 132.00 | PKLN | T4 | 4 | PERAK | 1 | TNB T | 1 | 35.3654 | 2.4572
63147 | SBGS132 132.00 | SBGS | T1 | 4 | PERAK | 1 | TNB T | 1 | 6.4284 | 0.9237
63147 | SBGS132 132.00 | SBGS | T2 | 4 | PERAK | 1 | TNB T | 1 | 6.3932 | 0.8885
63147 | SBGS132 132.00 | SBGS | T3 | 4 | PERAK | 1 | TNB T | 1 | 0 | 0
63147 | SBGS132 132.00 | SBGS | T4 | 4 | PERAK | 1 | TNB T | 1 | 11.9393 | 1.75
63125 | SIHY132 132.00 | SIHY | T1 | 4 | PERAK | 1 | TNB T | 1 | 0.1139 | 1.7189
63125 | SIHY132 132.00 | SIHY | T2 | 4 | PERAK | 1 | TNB T | 1 | 0.1035 | 1.6257
63111 | SIKD132 132.00 | SIKD | T1 | 4 | PERAK | 1 | TNB T | 1 | 18.1492 | 2.5608
63111 | SIKD132 132.00 | SIKD | T2 | 4 | PERAK | 1 | TNB T | 1 | 18.1264 | 2.5856
63111 | SIKD132 132.00 | SIKD | T3 | 4 | PERAK | 1 | TNB T | 1 | 23.8703 | -0.8512
63111 | SIKD132 132.00 | SIKD | T4 | 4 | PERAK | 1 | TNB T | 1 | 23.9211 | -0.8947
63157 | SRVR132 132.00 | SRVR | T5 | 4 | PERAK | 1 | TNB T | 1 | 7.6938 | 0.2175
63157 | SRVR132 132.00 | SRVR | T6 | 4 | PERAK | 1 | TNB T | 1 | 7.7031 | 0.2195
463159 | SSLS132 132.00 | SSLS | T1 | 4 | PERAK | 1 | TNB T | 1 | 15.5324 | 3.6942
63140 | SSPT132 132.00 | SSPT | T1 | 4 | PERAK | 1 | TNB T | 1 | 13.1084 | -2.772
63140 | SSPT132 132.00 | SSPT | T2 | 4 | PERAK | 1 | TNB T | 1 | 13.0877 | -2.7855
63126 | SYPS132 132.00 | SYPS | T1 | 4 | PERAK | 1 | TNB T | 1 | 0.3552 | -0.0197
63126 | SYPS132 132.00 | SYPS | T2 | 4 | PERAK | 1 | TNB T | 1 | 0.3572 | -0.0207
63134 | TASK132 132.00 | TASK | T1 | 4 | PERAK | 1 | TNB T | 1 | 4.8461 | 1.2012
63134 | TASK132 132.00 | TASK | T2 | 4 | PERAK | 1 | TNB T | 1 | 4.7219 | 1.1598
63134 | TASK132 132.00 | TASK | T3 | 4 | PERAK | 1 | TNB T | 1 | 9.4603 | 0.9423
63134 | TASK132 132.00 | TASK | T4 | 4 | PERAK | 1 | TNB T | 1 | 11.7529 | 1.2643
63135 | TCMT132 132.00 | TCMT | T1 | 4 | PERAK | 1 | TNB T | 1 | 6.563 | 1.3907
63135 | TCMT132 132.00 | TCMT | T2 | 4 | PERAK | 1 | TNB T | 1 | 9.917 | 1.5377
63135 | TCMT132 132.00 | TCMT | T3 | 4 | PERAK | 1 | TNB T | 1 | 2.5069 | 0.9444
63135 | TCMT132 132.00 | TCMT | T4 | 4 | PERAK | 1 | TNB T | 1 | 2.5173 | 0.9537
63150 | TINE132 132.00 | TINE | T1 | 4 | PERAK | 1 | TNB T | 1 | 8.6288 | 1.4311
63150 | TINE132 132.00 | TINE | T2 | 4 | PERAK | 1 | TNB T | 1 | 8.5884 | 1.4114
63130 | TINT132 132.00 | TINT | T1 | 4 | PERAK | 1 | TNB T | 1 | 10.6242 | 1.5015
63130 | TINT132 132.00 | TINT | T2 | 4 | PERAK | 1 | TNB T | 1 | 10.4544 | 1.3751
563130 | TINT132R 132.00 | TINT | T3 | 4 | PERAK | 1 | TNB T | 1 | 6.4719 | 0.7352
63206 | TMGR275 275.00 | TMGR | T1 | 4 | PERAK | 1 | TNB T | 1 | 6.0473 | -2.2781
63127 | TMOH132 132.00 | TMOH | T3 | 4 | PERAK | 1 | TNB T | 1 | 11.3905 | -0.5074
63127 | TMOH132 132.00 | TMOH | T4 | 4 | PERAK | 1 | TNB T | 1 | 11.2144 | -0.4763
63154 | TPID132 132.00 | TPID | T1 | 4 | PERAK | 1 | TNB T | 1 | 12.5244 | 1.8235
63154 | TPID132 132.00 | TPID | T2 | 4 | PERAK | 1 | TNB T | 1 | 12.6248 | 1.8183
63154 | TPID132 132.00 | TPID | T3 | 4 | PERAK | 1 | TNB T | 1 | 34.218 | 0.2651
63154 | TPID132 132.00 | TPID | T4 | 4 | PERAK | 1 | TNB T | 1 | 33.9716 | 0.3075
63121 | TPNG132 132.00 | TPNG | T1 | 4 | PERAK | 1 | TNB T | 1 | 9.5307 | 1.2126
563121 | TPNG132R 132.00 | TPNG | T2 | 4 | PERAK | 1 | TNB T | 1 | 15.5169 | 1.4963
74212 | UJLI275 275.00 | UJLI | T1 | 4 | PERAK | 1 | TNB T | 1 | 0.8305 | -1.3172
74212 | UJLI275 275.00 | UJLI | T2 | 4 | PERAK | 1 | TNB T | 1 | 0.8398 | -1.2581
51061 | ABBA132 132.00 | ABBA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 3.6853 | 0.2247
51061 | ABBA132 132.00 | ABBA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 9.9542 | 0.613
51061 | ABBA132 132.00 | ABBA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 27.8259 | 0.5447
51061 | ABBA132 132.00 | ABBA | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 27.5484 | 0.5416
51019 | ADAM132 132.00 | ADAM | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 12.9334 | 5.3256
51019 | ADAM132 132.00 | ADAM | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 12.4084 | -5.513
51028 | AHTM132 132.00 | AHTM | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 43.4909 | 3.121
51028 | AHTM132 132.00 | AHTM | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 44.3266 | 3.6978
51043 | BARG132 132.00 | BARG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 12.2593 | 1.0096
51043 | BARG132 132.00 | BARG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 5.746 | 0.5488
51043 | BARG132 132.00 | BARG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 18.202 | 1.5905
51043 | BARG132 132.00 | BARG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 17.998 | 1.546
51035 | BBDG132 132.00 | BBDG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 27.7327 | 7.3593
51035 | BBDG132 132.00 | BBDG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 27.6499 | 7.351
551035 | BBDG132_T 132.00 | BBDG | T7 | 5 | SELANGOR | 1 | TNB T | 1 | 18.3387 | 5.4778
51071 | BBST132 132.00 | BBST | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 5.5306 | 0.3355
51071 | BBST132 132.00 | BBST | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 3.9287 | 0.1967
51071 | BBST132 132.00 | BBST | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 20.2098 | -1.5346
51071 | BBST132 132.00 | BBST | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 20.1239 | -1.5388
51037 | BBTC132 132.00 | BBTC | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 38.708 | 5.6341
51037 | BBTC132 132.00 | BBTC | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 38.0753 | 5.5731
51087 | BBTG132 132.00 | BBTG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 6.3124 | 1.0717
51087 | BBTG132 132.00 | BBTG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 6.4698 | 0.8419
51087 | BBTG132 132.00 | BBTG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 20.0307 | 1.9426
51087 | BBTG132 132.00 | BBTG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 19.8681 | 1.9385
51078 | BCHG132 132.00 | BCHG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 16.8289 | 0.2133
51078 | BCHG132 132.00 | BCHG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 11.6928 | 1.3648
51078 | BCHG132 132.00 | BCHG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 26.4539 | 3.3695
51078 | BCHG132 132.00 | BCHG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 26.1008 | 3.3084
88194 | BCVS132 132.00 | BCVS | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 7.5726 | 1.1101
88194 | BCVS132 132.00 | BCVS | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 11.0084 | 1.8919
88194 | BCVS132 132.00 | BCVS | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 43.4019 | 7.8315
88194 | BCVS132 132.00 | BCVS | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 43.8937 | 7.8988
51060 | BHGT132 132.00 | BHGT | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 5.6238 | 1.167
51060 | BHGT132 132.00 | BHGT | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 9.627 | 0.4059
88177 | BJLL132 132.00 | BJLL | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 39.4245 | -0.4691
88177 | BJLL132 132.00 | BJLL | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 39.4804 | -0.4577
88177 | BJLL132 132.00 | BJLL | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 8.0168 | -0.1564
88177 | BJLL132 132.00 | BJLL | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 9.4023 | 0.9402
51083 | BJTG132 132.00 | BJTG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 8.1742 | 1.3068
51083 | BJTG132 132.00 | BJTG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 5.6818 | 0.6047
51083 | BJTG132 132.00 | BJTG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 35.82 | 1.7241
51083 | BJTG132 132.00 | BJTG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 35.1811 | 1.2996
51045 | BKPR132 132.00 | BKPR | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 14.6699 | 2.7223
51045 | BKPR132 132.00 | BKPR | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 16.307 | 2.6602
51045 | BKPR132 132.00 | BKPR | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 38.7349 | 2.1093
51045 | BKPR132 132.00 | BKPR | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 38.7432 | 2.1114
51062 | BLKG132 132.00 | BLKG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 8.6506 | 1.749
51062 | BLKG132 132.00 | BLKG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 5.0605 | 0.5322
51062 | BLKG132 132.00 | BLKG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 42.6936 | 5.9489
51062 | BLKG132 132.00 | BLKG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 41.9139 | 6.9762
51004 | BRGS132 132.00 | BRGS | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 8.0603 | 1.5967
51004 | BRGS132 132.00 | BRGS | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 10.8178 | 1.168
51004 | BRGS132 132.00 | BRGS | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51004 | BRGS132 132.00 | BRGS | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51053 | BRNG132 132.00 | BRNG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51053 | BRNG132 132.00 | BRNG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 19.6879 | 3.3188
51053 | BRNG132 132.00 | BRNG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51053 | BRNG132 132.00 | BRNG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51056 | BSTA132 132.00 | BSTA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 6.1623 | 0.6234
51056 | BSTA132 132.00 | BSTA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 11.1047 | 1.1587
51056 | BSTA132 132.00 | BSTA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 15.17 | 2.1466
51056 | BSTA132 132.00 | BSTA | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 15.227 | 2.1673
51001 | BTAI132 132.00 | BTAI | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 11.8761 | -7.7952
51001 | BTAI132 132.00 | BTAI | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51048 | BTGA132 132.00 | BTGA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 18.814 | 2.8393
51048 | BTGA132 132.00 | BTGA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 19.0863 | 2.0099
51048 | BTGA132 132.00 | BTGA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
151088 | BTIC-T 132.00 | BTIC | T7 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51088 | BTIC132 132.00 | BTIC | T7 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51008 | BTIN132 132.00 | BTIN | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 52.4149 | 7.8149
51008 | BTIN132 132.00 | BTIN | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 54.3067 | 7.8884
51112 | CBJN132 132.00 | CBJN | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 5.4633 | 0.2112
51112 | CBJN132 132.00 | CBJN | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 6.2637 | 0.4256
51112 | CBJN132 132.00 | CBJN | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 29.5593 | -1.0251
51112 | CBJN132 132.00 | CBJN | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 29.7043 | -1.0365
51006 | CBPS132 132.00 | CBPS | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 15.869 | 2.5732
51006 | CBPS132 132.00 | CBPS | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 12.0988 | 2.3703
51006 | CBPS132 132.00 | CBPS | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 44.9676 | 4.8648
51006 | CBPS132 132.00 | CBPS | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 44.1744 | 3.4451
51038 | CJYA132 132.00 | CJYA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 31.8343 | 4.4402
51038 | CJYA132 132.00 | CJYA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 33.5056 | 6.4667
51038 | CJYA132 132.00 | CJYA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 66.9274 | 7.7186
52008 | EGDC275 275.00 | EGDC | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 2.129 | 0.7506
51067 | ELMW132 132.00 | ELMW | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51067 | ELMW132 132.00 | ELMW | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
96169 | ESTK132 132.00 | ESTK | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 22.637 | 0.0601
96169 | ESTK132 132.00 | ESTK | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 22.8441 | 0.0311
51072 | HCOM132 132.00 | HCOM | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 38.7888 | 3.764
51072 | HCOM132 132.00 | HCOM | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 34.0078 | 5.9603
51072 | HCOM132 132.00 | HCOM | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 6.7442 | 1.1018
51072 | HCOM132 132.00 | HCOM | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 9.6643 | 1.3389
51047 | IGBK132 132.00 | IGBK | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 10.7733 | 2.0493
51047 | IGBK132 132.00 | IGBK | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 11.6069 | 2.7306
51047 | IGBK132 132.00 | IGBK | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 20.9937 | 2.5877
51047 | IGBK132 132.00 | IGBK | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 19.282 | 0.5654
51031 | KCPK132 132.00 | KCPK | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 31.1292 | 2.0679
51031 | KCPK132 132.00 | KCPK | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 31.0246 | 2.1217
51011 | KDSA132 132.00 | KDSA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 8.5201 | 1.4839
51011 | KDSA132 132.00 | KDSA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 10.7361 | 1.8225
51011 | KDSA132 132.00 | KDSA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 51.0346 | 7.0559
51011 | KDSA132 132.00 | KDSA | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 39.992 | 0.5436
51011 | KDSA132 132.00 | KDSA | T5 | 5 | SELANGOR | 1 | TNB T | 1 | 40.8152 | 13.0121
51055 | KJNG132 132.00 | KJNG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 12.6559 | 2.6157
51055 | KJNG132 132.00 | KJNG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 15.4838 | 2.9605
51055 | KJNG132 132.00 | KJNG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 39.6617 | 4.5624
51055 | KJNG132 132.00 | KJNG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 39.787 | 4.6049
51036 | KKMG132 132.00 | KKMG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 6.8622 | 0.8864
51036 | KKMG132 132.00 | KKMG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 7.7538 | 1.2654
51036 | KKMG132 132.00 | KKMG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 44.4291 | 4.0519
51036 | KKMG132 132.00 | KKMG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 45.1436 | 4.1037
51018 | KLIA132 132.00 | KLIA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 6.2534 | -0.0445
51018 | KLIA132 132.00 | KLIA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 4.9652 | -0.5902
51018 | KLIA132 132.00 | KLIA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 62.8278 | 2.0803
51018 | KLIA132 132.00 | KLIA | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
52020 | KLPP275 275.00 | KLPP | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
52020 | KLPP275 275.00 | KLPP | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
52020 | KLPP275 275.00 | KLPP | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51026 | KPNG132 132.00 | KPNG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 6.5754 | 1.0893
51026 | KPNG132 132.00 | KPNG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 6.5806 | 1.0987
51014 | KSBG132 132.00 | KSBG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 12.5554 | 0.934
51014 | KSBG132 132.00 | KSBG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 6.2368 | 0.7932
51014 | KSBG132 132.00 | KSBG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 25.9776 | 0.9848
51014 | KSBG132 132.00 | KSBG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 25.8895 | -0.3148
51016 | KSGR132 132.00 | KSGR | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 30.9656 | 4.2745
51016 | KSGR132 132.00 | KSGR | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 31.2338 | 4.3149
51069 | LGMR132 132.00 | LGMR | F1 | 5 | SELANGOR | 1 | TNB T | 1 | 1.7945 | 1.6061
51069 | LGMR132 132.00 | LGMR | F2 | 5 | SELANGOR | 1 | TNB T | 1 | 1.5419 | 1.7324
51085 | LKDG132 132.00 | LKDG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 11.2134 | 2.2698
51085 | LKDG132 132.00 | LKDG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 12.1588 | 1.838
51085 | LKDG132 132.00 | LKDG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 28.645 | 4.3895
51085 | LKDG132 132.00 | LKDG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 28.47 | 4.3822
51058 | LSHA132 132.00 | LSHA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 1.5398 | -3.3478
51058 | LSHA132 132.00 | LSHA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51057 | MERU132 132.00 | MERU | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 8.6112 | 1.8266
51057 | MERU132 132.00 | MERU | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 11.4267 | 2.7544
51057 | MERU132 132.00 | MERU | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 43.9352 | 3.8055
51057 | MERU132 132.00 | MERU | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 44.0532 | 3.8055
51022 | MHTA132 132.00 | MHTA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 7.6782 | 1.7438
51022 | MHTA132 132.00 | MHTA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 5.6807 | 0.5581
51022 | MHTA132 132.00 | MHTA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 31.2596 | 6.2865
51022 | MHTA132 132.00 | MHTA | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 31.3373 | 6.3756
51005 | NKST132 132.00 | NKST | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 29.2062 | 8.7324
51005 | NKST132 132.00 | NKST | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 29.3491 | 8.7841
51200 | NRWG132 132.00 | NRWG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 37.6476 | 5.1278
51200 | NRWG132 132.00 | NRWG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 37.5762 | 5.106
51200 | NRWG132 132.00 | NRWG | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 12.9852 | 2.2149
51200 | NRWG132 132.00 | NRWG | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 6.6593 | 1.9602
51025 | NSDA132 132.00 | NSDA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 31.0536 | 4.5231
51025 | NSDA132 132.00 | NSDA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 31.0919 | 4.5075
51025 | NSDA132 132.00 | NSDA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 4.6784 | 0.7756
51025 | NSDA132 132.00 | NSDA | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 6.0059 | 1.1763
51091 | NSPK132 132.00 | NSPK | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 26.3079 | 2.887
51091 | NSPK132 132.00 | NSPK | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 25.7756 | 2.8414
51091 | NSPK132 132.00 | NSPK | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 6.8012 | 1.0479
51091 | NSPK132 132.00 | NSPK | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 6.1778 | 0.9485
51023 | NUNI132 132.00 | NUNI | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 12.719 | 2.859
51023 | NUNI132 132.00 | NUNI | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 13.096 | 1.778
51023 | NUNI132 132.00 | NUNI | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 34.1166 | 4.1855
51023 | NUNI132 132.00 | NUNI | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 34.8124 | 4.026
88174 | PCHJ132 132.00 | PCHJ | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 30.6073 | 4.2735
88174 | PCHJ132 132.00 | PCHJ | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 30.6476 | 4.2393
88174 | PCHJ132 132.00 | PCHJ | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 5.0594 | 0.8481
88174 | PCHJ132 132.00 | PCHJ | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 5.0501 | 0.8388
51103 | PCHP132 132.00 | PCHP | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 25.6452 | 4.1793
551103 | PCHP132R 132.00 | PCHP | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 46.1988 | 4.1451
551103 | PCHP132R 132.00 | PCHP | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 46.3707 | 4.0467
63102 | PCTY132 132.00 | PCTY | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 7.8646 | 0.7041
63102 | PCTY132 132.00 | PCTY | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 12.3877 | 1.4777
63102 | PCTY132 132.00 | PCTY | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 7.3179 | -1.5719
63102 | PCTY132 132.00 | PCTY | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 10.1717 | 3.6439
51049 | PIDH132 132.00 | PIDH | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 41.4728 | 10.3508
51049 | PIDH132 132.00 | PIDH | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 41.335 | 10.326
51049 | PIDH132 132.00 | PIDH | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 6.8778 | 1.5377
51049 | PIDH132 132.00 | PIDH | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 12.9344 | 3.385
51049 | PIDH132 132.00 | PIDH | T5 | 5 | SELANGOR | 40 | CAPACITORS | 1 | 39.992 | 7.4556
51049 | PIDH132 132.00 | PIDH | T6 | 5 | SELANGOR | 40 | CAPACITORS | 1 | 38.1726 | 9.5628
51082 | PJST132 132.00 | PJST | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 26.5398 | 2.304
51082 | PJST132 132.00 | PJST | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 26.5481 | 2.3257
51082 | PJST132 132.00 | PJST | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 8.6257 | 1.37
51082 | PJST132 132.00 | PJST | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 11.2217 | 1.4808
51015 | PKLG132 132.00 | PKLG | N1 | 5 | SELANGOR | 1 | TNB T | 1 | 7.9495 | 0.9558
51015 | PKLG132 132.00 | PKLG | N2 | 5 | SELANGOR | 1 | TNB T | 1 | 7.8822 | 0.9299
51015 | PKLG132 132.00 | PKLG | N3 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51015 | PKLG132 132.00 | PKLG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51015 | PKLG132 132.00 | PKLG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51042 | PMRN132 132.00 | PMRN | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 13.0421 | 2.5577
51042 | PMRN132 132.00 | PMRN | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 14.1636 | 2.887
51042 | PMRN132 132.00 | PMRN | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 47.7158 | 8.2291
51042 | PMRN132 132.00 | PMRN | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 47.8411 | 8.2964
51039 | PNGA132 132.00 | PNGA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 35.267 | -1.749
51039 | PNGA132 132.00 | PNGA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 35.3333 | 12.6465
51009 | PROT132 132.00 | PROT | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 32.4039 | 7.7776
51009 | PROT132 132.00 | PROT | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 32.2796 | 7.76
51009 | PROT132 132.00 | PROT | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 49.7164 | 15.49
88176 | PTAI132 132.00 | PTAI | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
88176 | PTAI132 132.00 | PTAI | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
88176 | PTAI132 132.00 | PTAI | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 34.8342 | 2.6923
88176 | PTAI132 132.00 | PTAI | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 34.5877 | 2.6084
51052 | RSID132 132.00 | RSID | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 16.4002 | 3.0402
51052 | RSID132 132.00 | RSID | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 16.3112 | 3.0319
51218 | RWSS132 132.00 | RWSS | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 6.2586 | -2.0078
51034 | SBSR132 132.00 | SBSR | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 14.1739 | 0.7466
51034 | SBSR132 132.00 | SBSR | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 12.9406 | 1.4746
51034 | SBSR132 132.00 | SBSR | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 24.0464 | 0.7652
51034 | SBSR132 132.00 | SBSR | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 23.5576 | 0.7569
51032 | SDCA132 132.00 | SDCA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 17.6004 | 0.6845
51032 | SDCA132 132.00 | SDCA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 17.6449 | 0.7041
51027 | SHAB132 132.00 | SHAB | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 25.2341 | 3.5984
51027 | SHAB132 132.00 | SHAB | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 26.0252 | 3.3757
51017 | SHAE132 132.00 | SHAE | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 2.3765 | 0.058
51017 | SHAE132 132.00 | SHAE | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 5.6756 | 1.4041
51017 | SHAE132 132.00 | SHAE | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 23.7854 | 5.1723
51017 | SHAE132 132.00 | SHAE | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 24.0681 | 5.2023
51017 | SHAE132 132.00 | SHAE | T5 | 5 | SELANGOR | 1 | TNB T | 1 | 32.8543 | 8.0148
51003 | SHAN132 132.00 | SHAN | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51003 | SHAN132 132.00 | SHAN | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 0.007 | 0
51003 | SHAN132 132.00 | SHAN | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51007 | SHAS132 132.00 | SHAS | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 38.9275 | 7.3272
51007 | SHAS132 132.00 | SHAS | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 39.0476 | 7.3665
51041 | SHAW132 132.00 | SHAW | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 9.2294 | 1.8473
51041 | SHAW132 132.00 | SHAW | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 5.8288 | 0.6389
51041 | SHAW132 132.00 | SHAW | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 28.5911 | 3.8686
51041 | SHAW132 132.00 | SHAW | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 28.4565 | 3.9028
51002 | SHLB132 132.00 | SHLB | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 27.4096 | 5.3432
51002 | SHLB132 132.00 | SHLB | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 27.5132 | 5.3535
51075 | SJTC132 132.00 | SJTC | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 28.4607 | 4.7012
51075 | SJTC132 132.00 | SJTC | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 28.5301 | 4.7219
51054 | SMYH132 132.00 | SMYH | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 8.4383 | 0.6865
51054 | SMYH132 132.00 | SMYH | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 12.1516 | 1.9995
51030 | SRDG132 132.00 | SRDG | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 30.2914 | -3.091
51030 | SRDG132 132.00 | SRDG | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51029 | SSWW132 132.00 | SSWW | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 0 | 0
51029 | SSWW132 132.00 | SSWW | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 9.4634 | 1.7593
51013 | STIA132 132.00 | STIA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 33.1173 | 3.7361
51013 | STIA132 132.00 | STIA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 36.9797 | 6.184
51020 | TJYA132 132.00 | TJYA | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 26.4901 | 3.179
51020 | TJYA132 132.00 | TJYA | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 26.8805 | 4.0239
51020 | TJYA132 132.00 | TJYA | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 16.2263 | 2.4541
51084 | TMSY132 132.00 | TMSY | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 15.5138 | -0.7714
51084 | TMSY132 132.00 | TMSY | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 15.4766 | -0.787
51084 | TMSY132 132.00 | TMSY | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 1.6351 | 0.2268
51084 | TMSY132 132.00 | TMSY | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 2.3009 | 0.1419
51051 | TPGR132 132.00 | TPGR | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 16.6135 | 1.9198
51051 | TPGR132 132.00 | TPGR | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 9.2201 | 1.9933
51051 | TPGR132 132.00 | TPGR | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 45.2886 | 7.6441
51051 | TPGR132 132.00 | TPGR | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 45.5454 | 7.6741
51100 | UYAM132 132.00 | UYAM | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 11.7146 | 1.2726
51100 | UYAM132 132.00 | UYAM | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 12.6569 | 2.6519
51100 | UYAM132 132.00 | UYAM | T3 | 5 | SELANGOR | 1 | TNB T | 1 | 3.7961 | -1.7034
51100 | UYAM132 132.00 | UYAM | T4 | 5 | SELANGOR | 1 | TNB T | 1 | 3.763 | -1.7127
51046 | VMBR132 132.00 | VMBR | T1 | 5 | SELANGOR | 1 | TNB T | 1 | 41.5328 | 2.8932
51046 | VMBR132 132.00 | VMBR | T2 | 5 | SELANGOR | 1 | TNB T | 1 | 41.0751 | 2.8828
51061 | ABBA132 132.00 | ABBA | T5 | 6 | WPKL | 1 | TNB T | 1 | 17.3229 | 1.4414
51061 | ABBA132 132.00 | ABBA | T6 | 6 | WPKL | 1 | TNB T | 1 | 17.3322 | 1.458
51142 | AMDC132 132.00 | AMDC | T1 | 6 | WPKL | 1 | TNB T | 1 | 0.3925 | 0.8689
51142 | AMDC132 132.00 | AMDC | T2 | 6 | WPKL | 1 | TNB T | 1 | 0.9299 | 0.9715
88120 | AMPG132 132.00 | AMPG | T3 | 6 | WPKL | 1 | TNB T | 1 | 42.5704 | 5.6611
88120 | AMPG132 132.00 | AMPG | T4 | 6 | WPKL | 1 | TNB T | 1 | 42.4761 | 5.5824
88120 | AMPG132 132.00 | AMPG | T5 | 6 | WPKL | 1 | TNB T | 1 | 30.0233 | -1.1867
88120 | AMPG132 132.00 | AMPG | T6 | 6 | WPKL | 40 | CAPACITORS | 1 | 29.4548 | 11.9269
88123 | BBCC132 132.00 | BBCC | T1 | 6 | WPKL | 1 | TNB T | 1 | 4.1254 | 0.3479
88123 | BBCC132 132.00 | BBCC | T2 | 6 | WPKL | 1 | TNB T | 1 | 4.1648 | 0.3479
88141 | BFLD132 132.00 | BFLD | T1 | 6 | WPKL | 1 | TNB T | 1 | 22.2001 | 3.4927
88141 | BFLD132 132.00 | BFLD | T2 | 6 | WPKL | 1 | TNB T | 1 | 22.55 | 3.5549
88114 | BMKM132 132.00 | BMKM | T1 | 6 | WPKL | 1 | TNB T | 1 | 14.1749 | 0.9734
88114 | BMKM132 132.00 | BMKM | T2 | 6 | WPKL | 1 | TNB T | 1 | 14.1749 | 0.9237
51053 | BRNG132 132.00 | BRNG | T5 | 6 | WPKL | 1 | TNB T | 1 | 34.0006 | 2.2243
51053 | BRNG132 132.00 | BRNG | T6 | 6 | WPKL | 1 | TNB T | 1 | 33.6754 | 2.2066
88136 | BTRZ132 132.00 | BTRZ | T1 | 6 | WPKL | 1 | TNB T | 1 | 15.6692 | 2.188
88136 | BTRZ132 132.00 | BTRZ | T2 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
88136 | BTRZ132 132.00 | BTRZ | T3 | 6 | WPKL | 1 | TNB T | 1 | 41.1642 | 1.6185
88136 | BTRZ132 132.00 | BTRZ | T4 | 6 | WPKL | 1 | TNB T | 1 | 41.4603 | 1.5998
51089 | CBJC132 132.00 | CBJC | T2 | 6 | WPKL | 1 | TNB T | 1 | 27.3071 | -4.1451
51089 | CBJC132 132.00 | CBJC | T3 | 6 | WPKL | 1 | TNB T | 1 | 6.2461 | -0.0828
51089 | CBJC132 132.00 | CBJC | T4 | 6 | WPKL | 1 | TNB T | 1 | 6.2161 | -0.0859
88164 | COCH132 132.00 | COCH | T1 | 6 | WPKL | 1 | TNB T | 1 | 4.784 | 0.5592
88164 | COCH132 132.00 | COCH | T2 | 6 | WPKL | 1 | TNB T | 1 | 4.7736 | 0.5177
88104 | DCTY132 132.00 | DCTY | T1 | 6 | WPKL | 40 | CAPACITORS | 1 | 12.8951 | 1.2892
88104 | DCTY132 132.00 | DCTY | T2 | 6 | WPKL | 40 | CAPACITORS | 1 | 12.9489 | 1.2695
88195 | DDSA132 132.00 | DDSA | T1 | 6 | WPKL | 1 | TNB T | 1 | 7.1957 | 0.7777
88195 | DDSA132 132.00 | DDSA | T2 | 6 | WPKL | 1 | TNB T | 1 | 5.804 | 0.643
88195 | DDSA132 132.00 | DDSA | T3 | 6 | WPKL | 1 | TNB T | 1 | 30.6777 | -0.5302
88195 | DDSA132 132.00 | DDSA | T4 | 6 | WPKL | 1 | TNB T | 1 | 30.6943 | -0.5385
88112 | DMHT132 132.00 | DMHT | T1 | 6 | WPKL | 1 | TNB T | 1 | 15.1669 | 0.6979
88112 | DMHT132 132.00 | DMHT | T2 | 6 | WPKL | 1 | TNB T | 1 | 15.0996 | 0.7072
88112 | DMHT132 132.00 | DMHT | T3 | 6 | WPKL | 1 | TNB T | 1 | 6.6458 | 0.7052
88112 | DMHT132 132.00 | DMHT | T4 | 6 | WPKL | 1 | TNB T | 1 | 6.621 | 0.1294
88113 | DWGI132 132.00 | DWGI | T1 | 6 | WPKL | 1 | TNB T | 1 | 5.9924 | 1.0707
88113 | DWGI132 132.00 | DWGI | T2 | 6 | WPKL | 1 | TNB T | 1 | 5.9407 | 0.9785
88133 | GWAY132 132.00 | GWAY | T1 | 6 | WPKL | 1 | TNB T | 1 | 13.3186 | 1.3617
88133 | GWAY132 132.00 | GWAY | T2 | 6 | WPKL | 1 | TNB T | 1 | 13.302 | 1.4352
88156 | HKCK132 132.00 | HKCK | T1 | 6 | WPKL | 1 | TNB T | 1 | 7.5384 | 0.9516
88156 | HKCK132 132.00 | HKCK | T2 | 6 | WPKL | 1 | TNB T | 1 | 7.877 | 1.0469
88156 | HKCK132 132.00 | HKCK | T3 | 6 | WPKL | 1 | TNB T | 1 | 42.1116 | 6.7463
88156 | HKCK132 132.00 | HKCK | T4 | 6 | WPKL | 1 | TNB T | 1 | 41.7016 | 6.6469
51219 | ICNC132 132.00 | ICNC | T1 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
51219 | ICNC132 132.00 | ICNC | T2 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
88161 | IMBI132 132.00 | IMBI | T1 | 6 | WPKL | 1 | TNB T | 1 | 3.2194 | 0.5509
88161 | IMBI132 132.00 | IMBI | T2 | 6 | WPKL | 1 | TNB T | 1 | 10.9939 | 3.2587
88161 | IMBI132 132.00 | IMBI | T3 | 6 | WPKL | 1 | TNB T | 1 | 25.4443 | 4.405
88161 | IMBI132 132.00 | IMBI | T4 | 6 | WPKL | 1 | TNB T | 1 | 25.6182 | 7.9143
88161 | IMBI132 132.00 | IMBI | T5 | 6 | WPKL | 1 | TNB T | 1 | 33.9478 | 8.8411
51101 | IOIM132 132.00 | IOIM | T1 | 6 | WPKL | 1 | TNB T | 1 | 16.6208 | 3.6087
51101 | IOIM132 132.00 | IOIM | T2 | 6 | WPKL | 1 | TNB T | 1 | 16.5214 | 3.5984
51066 | JDHL132 132.00 | JDHL | T1 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
51066 | JDHL132 132.00 | JDHL | T2 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
88157 | JING132 132.00 | JING | T1 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
88157 | JING132 132.00 | JING | T2 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
51092 | KEST132 132.00 | KEST | T1 | 6 | WPKL | 1 | TNB T | 1 | 45.9347 | 4.6183
51092 | KEST132 132.00 | KEST | T2 | 6 | WPKL | 1 | TNB T | 1 | 45.7483 | 4.5976
88146 | KLCC132 132.00 | KLCC | T3 | 6 | WPKL | 1 | TNB T | 1 | 20.4801 | 4.1337
88146 | KLCC132 132.00 | KLCC | T4 | 6 | WPKL | 1 | TNB T | 1 | 20.4345 | 4.1337
588146 | KLCC132R 132.00 | KLCC | T1 | 6 | WPKL | 1 | TNB T | 1 | 6.3859 | 1.0044
588146 | KLCC132R 132.00 | KLCC | T2 | 6 | WPKL | 1 | TNB T | 1 | 6.9161 | 1.5367
88121 | KLJT132 132.00 | KLJT | T1 | 6 | WPKL | 1 | TNB T | 1 | 18.8875 | 1.924
88121 | KLJT132 132.00 | KLJT | T2 | 6 | WPKL | 1 | TNB T | 1 | 18.8129 | 1.9478
88121 | KLJT132 132.00 | KLJT | T4 | 6 | WPKL | 1 | TNB T | 1 | 18.495 | -1.8484
88163 | KLPV132 132.00 | KLPV | T1 | 6 | WPKL | 1 | TNB T | 1 | 28.5694 | 3.5828
88163 | KLPV132 132.00 | KLPV | T2 | 6 | WPKL | 1 | TNB T | 1 | 28.6108 | 3.6346
588124 | KULE132R 132.00 | KULE | T1 | 6 | WPKL | 1 | TNB T | 1 | 39.3697 | 6.4781
588124 | KULE132R 132.00 | KULE | T2 | 6 | WPKL | 1 | TNB T | 1 | 39.3707 | 6.5102
88111 | KULN132L 132.00 | KULN | T1 | 6 | WPKL | 1 | TNB T | 1 | 38.272 | 5.2686
88111 | KULN132L 132.00 | KULN | T2 | 6 | WPKL | 1 | TNB T | 1 | 38.2026 | 5.2593
588111 | KULN132R 132.00 | KULN | T3 | 6 | WPKL | 1 | TNB T | 1 | 16.6011 | 0.7259
588111 | KULN132R 132.00 | KULN | T4 | 6 | WPKL | 1 | TNB T | 1 | 16.482 | 0.7756
88117 | KULS132 132.00 | KULS | T1 | 6 | WPKL | 1 | TNB T | 1 | 12.5948 | 1.6568
88117 | KULS132 132.00 | KULS | T2 | 6 | WPKL | 1 | TNB T | 1 | 6.5506 | 0.554
88117 | KULS132 132.00 | KULS | T3 | 6 | WPKL | 1 | TNB T | 1 | 41.9574 | 4.6142
88117 | KULS132 132.00 | KULS | T4 | 6 | WPKL | 1 | TNB T | 1 | 41.9077 | 4.6566
51081 | MCRS132 132.00 | MCRS | T1 | 6 | WPKL | 1 | TNB T | 1 | 29.6691 | 4.2528
51081 | MCRS132 132.00 | MCRS | T2 | 6 | WPKL | 1 | TNB T | 1 | 25.7125 | 1.8815
88129 | MDAM132 132.00 | MDAM | T1 | 6 | WPKL | 1 | TNB T | 1 | 18.2683 | 7.9547
88129 | MDAM132 132.00 | MDAM | T2 | 6 | WPKL | 1 | TNB T | 1 | 17.3322 | -4.2114
88128 | MJLR132 132.00 | MJLR | T1 | 6 | WPKL | 1 | TNB T | 1 | 49.94 | 7.8211
88128 | MJLR132 132.00 | MJLR | T2 | 6 | WPKL | 1 | TNB T | 1 | 49.3467 | 7.7176
88105 | MTRE132 132.00 | MTRE | T1 | 6 | WPKL | 1 | TNB T | 1 | 9.7119 | 0.497
88105 | MTRE132 132.00 | MTRE | T2 | 6 | WPKL | 1 | TNB T | 1 | 9.6519 | 0.5064
88139 | MVLY132 132.00 | MVLY | T1 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
88139 | MVLY132 132.00 | MVLY | T2 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
88139 | MVLY132 132.00 | MVLY | T3 | 6 | WPKL | 1 | TNB T | 1 | 28.7982 | 5.7356
88139 | MVLY132 132.00 | MVLY | T4 | 6 | WPKL | 1 | TNB T | 1 | 28.6295 | 5.7263
88116 | MWSN132 132.00 | MWSN | T1 | 6 | WPKL | 1 | TNB T | 1 | 1.4311 | -0.2589
88116 | MWSN132 132.00 | MWSN | T2 | 6 | WPKL | 1 | TNB T | 1 | 1.4217 | -0.2485
51073 | PJYC132 132.00 | PJYC | T1 | 6 | WPKL | 1 | TNB T | 1 | 23.6653 | -0.5105
51073 | PJYC132 132.00 | PJYC | T2 | 6 | WPKL | 1 | TNB T | 1 | 23.8517 | -0.5022
88175 | PMJU132 132.00 | PMJU | T1 | 6 | WPKL | 1 | TNB T | 1 | 16.3951 | 3.1137
88175 | PMJU132 132.00 | PMJU | T2 | 6 | WPKL | 1 | TNB T | 1 | 4.4868 | 0.4567
88175 | PMJU132 132.00 | PMJU | T3 | 6 | WPKL | 1 | TNB T | 1 | 37.1154 | 1.6754
88175 | PMJU132 132.00 | PMJU | T4 | 6 | WPKL | 1 | TNB T | 1 | 37.3774 | 1.7417
88175 | PMJU132 132.00 | PMJU | T5 | 6 | WPKL | 1 | TNB T | 1 | 36.0074 | 3.7123
88175 | PMJU132 132.00 | PMJU | T6 | 6 | WPKL | 1 | TNB T | 1 | 35.6936 | 3.6522
88119 | PULU132 132.00 | PULU | T1 | 6 | WPKL | 1 | TNB T | 1 | 46.3686 | 6.9451
88119 | PULU132 132.00 | PULU | T2 | 6 | WPKL | 1 | TNB T | 1 | 46.1988 | 6.8892
88179 | PVBJ132 132.00 | PVBJ | T1 | 6 | WPKL | 1 | TNB T | 1 | 17.1147 | 1.2488
88179 | PVBJ132 132.00 | PVBJ | T2 | 6 | WPKL | 1 | TNB T | 1 | 17.1634 | 1.2498
88107 | SCTY132 132.00 | SCTY | T1 | 6 | WPKL | 1 | TNB T | 1 | 17.1303 | 1.9757
88107 | SCTY132 132.00 | SCTY | T2 | 6 | WPKL | 1 | TNB T | 1 | 17.0774 | 1.9633
88173 | SDAM132 132.00 | SDAM | T1 | 6 | WPKL | 1 | TNB T | 1 | 27.8943 | 2.8414
88173 | SDAM132 132.00 | SDAM | T2 | 6 | WPKL | 1 | TNB T | 1 | 27.6488 | 2.9139
88122 | SGBT132 132.00 | SGBT | T1 | 6 | WPKL | 1 | TNB T | 1 | 40.1111 | 5.4105
88122 | SGBT132 132.00 | SGBT | T2 | 6 | WPKL | 1 | TNB T | 1 | 39.6472 | 5.3608
88142 | SHMS132 132.00 | SHMS | T1 | 6 | WPKL | 40 | CAPACITORS | 1 | 28.2235 | 4.231
88142 | SHMS132 132.00 | SHMS | T2 | 6 | WPKL | 40 | CAPACITORS | 1 | 28.1138 | 4.2145
88132 | SMTN132 132.00 | SMTN | T1 | 6 | WPKL | 1 | TNB T | 1 | 2.3382 | -1.3762
88132 | SMTN132 132.00 | SMTN | T2 | 6 | WPKL | 1 | TNB T | 1 | 2.3527 | -1.371
88162 | SPKC132 132.00 | SPKC | T3 | 6 | WPKL | 1 | TNB T | 1 | 49.6522 | 7.7248
88162 | SPKC132 132.00 | SPKC | T4 | 6 | WPKL | 1 | TNB T | 1 | 49.4036 | 7.6938
88162 | SPKC132 132.00 | SPKC | T5 | 6 | WPKL | 1 | TNB T | 1 | 55.7688 | 5.3805
51050 | SRDN132 132.00 | SRDN | T1 | 6 | WPKL | 1 | TNB T | 1 | 24.2483 | 1.3731
51050 | SRDN132 132.00 | SRDN | T2 | 6 | WPKL | 1 | TNB T | 1 | 24.2006 | 1.3638
51130 | SRDR132 132.00 | SRDR | T1 | 6 | WPKL | 1 | TNB T | 1 | 27.8539 | 3.1179
51130 | SRDR132 132.00 | SRDR | T2 | 6 | WPKL | 1 | TNB T | 1 | 27.9781 | 3.1303
88118 | SRYA132 132.00 | SRYA | T1 | 6 | WPKL | 1 | TNB T | 1 | 8.7137 | 1.1825
88118 | SRYA132 132.00 | SRYA | T2 | 6 | WPKL | 1 | TNB T | 1 | 8.6619 | 1.1732
88118 | SRYA132 132.00 | SRYA | T3 | 6 | WPKL | 1 | TNB T | 1 | 36.3325 | 5.6041
88118 | SRYA132 132.00 | SRYA | T4 | 6 | WPKL | 1 | TNB T | 1 | 36.578 | 5.6683
88127 | TMWT132 132.00 | TMWT | T1 | 6 | WPKL | 1 | TNB T | 1 | 12.7439 | -1.1929
88127 | TMWT132 132.00 | TMWT | T2 | 6 | WPKL | 1 | TNB T | 1 | 12.8433 | -1.1929
88134 | TNHQ132 132.00 | TNHQ | T1 | 6 | WPKL | 1 | TNB T | 1 | 22.9032 | 1.8608
88134 | TNHQ132 132.00 | TNHQ | T2 | 6 | WPKL | 1 | TNB T | 1 | 23.0999 | 1.8587
88137 | TWSA132 132.00 | TWSA | T1 | 6 | WPKL | 1 | TNB T | 1 | 25.6452 | 3.0226
88137 | TWSA132 132.00 | TWSA | T2 | 6 | WPKL | 1 | TNB T | 1 | 25.612 | 3.0081
88160 | VCTY132 132.00 | VCTY | T1 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
88160 | VCTY132 132.00 | VCTY | T2 | 6 | WPKL | 1 | TNB T | 1 | 0 | 0
88160 | VCTY132 132.00 | VCTY | T3 | 6 | WPKL | 1 | TNB T | 1 | 26.2675 | 4.6639
88160 | VCTY132 132.00 | VCTY | T4 | 6 | WPKL | 1 | TNB T | 1 | 26.574 | 4.7167
88159 | WMJU132 132.00 | WMJU | T1 | 6 | WPKL | 1 | TNB T | 1 | 48.0243 | 7.7538
88159 | WMJU132 132.00 | WMJU | T2 | 6 | WPKL | 1 | TNB T | 1 | 48.0855 | 7.7621
96152 | AMID132 132.00 | AMID | T1 | 7 | NS | 1 | TNB T | 1 | 6.7225 | 1.3234
96152 | AMID132 132.00 | AMID | T2 | 7 | NS | 1 | TNB T | 1 | 7.4691 | 2.0814
96152 | AMID132 132.00 | AMID | T3 | 7 | NS | 1 | TNB T | 1 | 31.9555 | 4.9269
96152 | AMID132 132.00 | AMID | T4 | 7 | NS | 1 | TNB T | 1 | 31.6034 | 4.9145
96138 | BAHA132 132.00 | BAHA | T1 | 7 | NS | 1 | TNB T | 1 | 12.4001 | 0.7487
96138 | BAHA132 132.00 | BAHA | T2 | 7 | NS | 1 | TNB T | 1 | 12.3835 | 0.7611
96138 | BAHA132 132.00 | BAHA | T3 | 7 | NS | 1 | TNB T | 1 | 5.4177 | -2.4158
96138 | BAHA132 132.00 | BAHA | T4 | 7 | NS | 1 | TNB T | 1 | 5.4674 | -2.4314
96146 | BBNL132 132.00 | BBNL | T1 | 7 | NS | 1 | TNB T | 1 | 1.1059 | -0.4908
96146 | BBNL132 132.00 | BBNL | T2 | 7 | NS | 1 | TNB T | 1 | 2.1 | -0.1781
96192 | BKPY132 132.00 | BKPY | T1 | 7 | NS | 1 | TNB T | 1 | 9.4189 | 1.9447
96192 | BKPY132 132.00 | BKPY | T2 | 7 | NS | 1 | TNB T | 1 | 12.9096 | 1.8629
96176 | CMBG132 132.00 | CMBG | T4 | 7 | NS | 1 | TNB T | 1 | 18.7322 | 1.8743
96140 | GMAS132 132.00 | GMAS | T1 | 7 | NS | 1 | TNB T | 1 | 13.185 | 2.0316
96140 | GMAS132 132.00 | GMAS | T2 | 7 | NS | 1 | TNB T | 1 | 8.3409 | 1.7138
96112 | KKWG132 132.00 | KKWG | T1 | 7 | NS | 1 | TNB T | 1 | 4.9932 | -1.1297
96112 | KKWG132 132.00 | KKWG | T2 | 7 | NS | 1 | TNB T | 1 | 5.0066 | -1.1504
96132 | KLAT132 132.00 | KLAT | T1 | 7 | NS | 1 | TNB T | 1 | 13.7411 | 1.8277
96132 | KLAT132 132.00 | KLAT | T2 | 7 | NS | 1 | TNB T | 1 | 9.5856 | 1.2146
96137 | KPLH132 132.00 | KPLH | T1 | 7 | NS | 1 | TNB T | 1 | 15.5283 | 0.147
96137 | KPLH132 132.00 | KPLH | T2 | 7 | NS | 1 | TNB T | 1 | 12.6579 | -0.4618
96134 | LKUT132 132.00 | LKUT | T1 | 7 | NS | 1 | TNB T | 1 | 12.0335 | 0.5768
96134 | LKUT132 132.00 | LKUT | T2 | 7 | NS | 1 | TNB T | 1 | 0 | 0
96134 | LKUT132 132.00 | LKUT | T3 | 7 | NS | 1 | TNB T | 1 | 14.0103 | 1.7293
96134 | LKUT132 132.00 | LKUT | T4 | 7 | NS | 1 | TNB T | 1 | 14.0621 | 1.7189
96156 | MTIN132 132.00 | MTIN | T3 | 7 | NS | 1 | TNB T | 1 | 0 | 0
96156 | MTIN132 132.00 | MTIN | T4 | 7 | NS | 1 | TNB T | 1 | 19.9934 | 2.2936
96125 | NLAI132 132.00 | NLAI | T1 | 7 | NS | 1 | TNB T | 1 | 9.9377 | 1.8825
96125 | NLAI132 132.00 | NLAI | T2 | 7 | NS | 1 | TNB T | 1 | 5.0035 | 0.8098
96136 | PBSR132 132.00 | PBSR | T1 | 7 | NS | 1 | TNB T | 1 | 13.2223 | -1.721
96136 | PBSR132 132.00 | PBSR | T2 | 7 | NS | 1 | TNB T | 1 | 12.3825 | -0.2185
96188 | PJAM132 132.00 | PJAM | T1 | 7 | NS | 1 | TNB T | 1 | 7.5716 | -0.3635
96188 | PJAM132 132.00 | PJAM | T2 | 7 | NS | 1 | TNB T | 1 | 7.1501 | 0.8626
96188 | PJAM132 132.00 | PJAM | T3 | 7 | NS | 1 | TNB T | 1 | 2.7751 | -3.1376
96188 | PJAM132 132.00 | PJAM | T4 | 7 | NS | 1 | TNB T | 1 | 2.9615 | 2.2781
96158 | PROI132 132.00 | PROI | T1 | 7 | NS | 1 | TNB T | 1 | 12.2489 | 1.5274
96158 | PROI132 132.00 | PROI | T2 | 7 | NS | 1 | TNB T | 1 | 15.4734 | 2.7969
96158 | PROI132 132.00 | PROI | T3 | 7 | NS | 1 | TNB T | 1 | 27.2626 | 3.3229
96158 | PROI132 132.00 | PROI | T4 | 7 | NS | 1 | TNB T | 1 | 27.3392 | 3.0195
96117 | RASA132 132.00 | RASA | T1 | 7 | NS | 1 | TNB T | 1 | 9.685 | 1.1722
96117 | RASA132 132.00 | RASA | T2 | 7 | NS | 1 | TNB T | 1 | 9.6726 | 1.0583
96142 | RTAU132 132.00 | RTAU | T1 | 7 | NS | 1 | TNB T | 1 | 8.7707 | 1.109
96142 | RTAU132 132.00 | RTAU | T2 | 7 | NS | 1 | TNB T | 1 | 8.7727 | 1.1018
96149 | SBAN132 132.00 | SBAN | T1 | 7 | NS | 1 | TNB T | 1 | 13.0193 | 1.839
96149 | SBAN132 132.00 | SBAN | T2 | 7 | NS | 1 | TNB T | 1 | 17.2773 | 2.1859
96150 | SDYN132 132.00 | SDYN | T1 | 7 | NS | 40 | CAPACITORS | 1 | 44.7532 | 5.4384
96150 | SDYN132 132.00 | SDYN | T2 | 7 | NS | 40 | CAPACITORS | 1 | 45.0318 | 5.4674
51079 | SLTI132 132.00 | SLTI | T1 | 7 | NS | 1 | TNB T | 1 | 12.6455 | 0.3645
51079 | SLTI132 132.00 | SLTI | T2 | 7 | NS | 1 | TNB T | 1 | 15.605 | 1.7396
51079 | SLTI132 132.00 | SLTI | T3 | 7 | NS | 40 | CAPACITORS | 1 | 4.0281 | -0.5592
51079 | SLTI132 132.00 | SLTI | T4 | 7 | NS | 40 | CAPACITORS | 1 | 4.0281 | -0.5592
96133 | SMRK132 132.00 | SMRK | T1 | 7 | NS | 1 | TNB T | 1 | 11.5406 | 1.8535
96133 | SMRK132 132.00 | SMRK | T2 | 7 | NS | 1 | TNB T | 1 | 10.8013 | 2.3713
96143 | SNWG132 132.00 | SNWG | T1 | 7 | NS | 1 | TNB T | 1 | 2.7027 | -0.9423
96143 | SNWG132 132.00 | SNWG | T2 | 7 | NS | 1 | TNB T | 1 | 2.6923 | -0.9216
96139 | SPTG132 132.00 | SPTG | T1 | 7 | NS | 1 | TNB T | 1 | 6.0276 | -0.7859
96139 | SPTG132 132.00 | SPTG | T2 | 7 | NS | 1 | TNB T | 1 | 6.0991 | -0.7777
96139 | SPTG132 132.00 | SPTG | T3 | 7 | NS | 1 | TNB T | 1 | 0 | 0
96139 | SPTG132 132.00 | SPTG | T4 | 7 | NS | 1 | TNB T | 1 | 0 | 0
96190 | STRA132 132.00 | STRA | T1 | 7 | NS | 1 | TNB T | 1 | 13.0794 | 1.3845
96190 | STRA132 132.00 | STRA | T2 | 7 | NS | 1 | TNB T | 1 | 6.9969 | 1.3534
96131 | TJGS132 132.00 | TJGS | T1 | 7 | NS | 1 | TNB T | 1 | 11.1792 | 1.283
96131 | TJGS132 132.00 | TJGS | T2 | 7 | NS | 1 | TNB T | 1 | 11.4112 | -0.1294
96915 | TJGSGT2A 15.750 | TJGS | X1 | 7 | NS | 1 | TNB T | 1 | 0 | 0
96135 | TJID132 132.00 | TJID | T1 | 7 | NS | 1 | TNB T | 1 | 11.1275 | 1.4963
96135 | TJID132 132.00 | TJID | T2 | 7 | NS | 1 | TNB T | 1 | 7.8615 | 1.8784
96135 | TJID132 132.00 | TJID | T3 | 7 | NS | 1 | TNB T | 1 | 19.9675 | 3.2018
96135 | TJID132 132.00 | TJID | T4 | 7 | NS | 1 | TNB T | 1 | 19.9893 | 3.1966
96144 | TKMG132 132.00 | TKMG | T1 | 7 | NS | 1 | TNB T | 1 | 6.8529 | 0.4142
96144 | TKMG132 132.00 | TKMG | T2 | 7 | NS | 1 | TNB T | 1 | 6.827 | 0.3956
96129 | TTJF132 132.00 | TTJF | T1 | 7 | NS | 1 | TNB T | 1 | 14.8677 | 2.5535
96129 | TTJF132 132.00 | TTJF | T2 | 7 | NS | 1 | TNB T | 1 | 14.9029 | 2.5411
96165 | AFMS132 132.00 | AFMS | T1 | 8 | MELAKA | 1 | TNB T | 1 | 5.1319 | -0.6627
96165 | AFMS132 132.00 | AFMS | T2 | 8 | MELAKA | 1 | TNB T | 1 | 8.0852 | 0.6213
96105 | AKRH132 132.00 | AKRH | T1 | 8 | MELAKA | 1 | TNB T | 1 | 12.1278 | 2.3464
96105 | AKRH132 132.00 | AKRH | T2 | 8 | MELAKA | 1 | TNB T | 1 | 8.5356 | 1.3234
96107 | BBDM132 132.00 | BBDM | T1 | 8 | MELAKA | 1 | TNB T | 1 | 13.9616 | 3.0195
96107 | BBDM132 132.00 | BBDM | T2 | 8 | MELAKA | 1 | TNB T | 1 | 14.7621 | 4.5686
96107 | BBDM132 132.00 | BBDM | T3 | 8 | MELAKA | 1 | TNB T | 1 | 9.4261 | 2.0006
96107 | BBDM132 132.00 | BBDM | T4 | 8 | MELAKA | 1 | TNB T | 1 | 7.3272 | 2.4469
96111 | BMKA132 132.00 | BMKA | T1 | 8 | MELAKA | 1 | TNB T | 1 | 5.6828 | 0.3117
96111 | BMKA132 132.00 | BMKA | T2 | 8 | MELAKA | 1 | TNB T | 1 | 8.8483 | 1.4642
96101 | BRBI132 132.00 | BRBI | T1 | 8 | MELAKA | 1 | TNB T | 1 | 6.6624 | 0.6213
96101 | BRBI132 132.00 | BRBI | T2 | 8 | MELAKA | 1 | TNB T | 1 | 9.1227 | 1.6185
96101 | BRBI132 132.00 | BRBI | T3 | 8 | MELAKA | 1 | TNB T | 1 | 10.1531 | 0.6244
96101 | BRBI132 132.00 | BRBI | T4 | 8 | MELAKA | 1 | TNB T | 1 | 10.1313 | 0.6265
96122 | BVTA132 132.00 | BVTA | T1 | 8 | MELAKA | 1 | TNB T | 1 | 3.3695 | 0.7735
96122 | BVTA132 132.00 | BVTA | T2 | 8 | MELAKA | 1 | TNB T | 1 | 8.5501 | 1.2209
96191 | CHNG132 132.00 | CHNG | T1 | 8 | MELAKA | 1 | TNB T | 1 | 7.3438 | 1.6102
96191 | CHNG132 132.00 | CHNG | T2 | 8 | MELAKA | 1 | TNB T | 1 | 10.6045 | 0.4856
96191 | CHNG132 132.00 | CHNG | T3 | 8 | MELAKA | 1 | TNB T | 1 | 31.8406 | 4.1731
96191 | CHNG132 132.00 | CHNG | T4 | 8 | MELAKA | 1 | TNB T | 1 | 31.8509 | 4.1793
96921 | EMPP_GT1 24.000 | EMPP | X1 | 8 | MELAKA | 1 | TNB T | 1 | 0 | 0
96922 | EMPP_GT2 24.000 | EMPP | X1 | 8 | MELAKA | 1 | TNB T | 1 | 0 | 0
96923 | EMPP_GT3 24.000 | EMPP | X1 | 8 | MELAKA | 1 | TNB T | 1 | 0 | 0
96106 | HPGH132 132.00 | HPGH | T1 | 8 | MELAKA | 40 | CAPACITORS | 1 | 5.9893 | 0.3272
96106 | HPGH132 132.00 | HPGH | T2 | 8 | MELAKA | 40 | CAPACITORS | 1 | 6.0111 | 0.3303
96109 | JSIN132 132.00 | JSIN | T1 | 8 | MELAKA | 1 | TNB T | 1 | 6.1726 | -0.408
96109 | JSIN132 132.00 | JSIN | T2 | 8 | MELAKA | 1 | TNB T | 1 | 11.8078 | 0.4908
96109 | JSIN132 132.00 | JSIN | T3 | 8 | MELAKA | 1 | TNB T | 1 | 8.6236 | -3.1065
96109 | JSIN132 132.00 | JSIN | T4 | 8 | MELAKA | 1 | TNB T | 1 | 8.7034 | -3.1407
96118 | KGDK132 132.00 | KGDK | T1 | 8 | MELAKA | 1 | TNB T | 1 | 0 | 0
96118 | KGDK132 132.00 | KGDK | T2 | 8 | MELAKA | 1 | TNB T | 1 | 7.7973 | -0.4401
96126 | KLMK132 132.00 | KLMK | T1 | 8 | MELAKA | 1 | TNB T | 1 | 9.7606 | 1.4383
96126 | KLMK132 132.00 | KLMK | T2 | 8 | MELAKA | 1 | TNB T | 1 | 8.0769 | 0.1046
96126 | KLMK132 132.00 | KLMK | T3 | 8 | MELAKA | 40 | CAPACITORS | 1 | 2.5991 | -0.787
96126 | KLMK132 132.00 | KLMK | T4 | 8 | MELAKA | 40 | CAPACITORS | 1 | 2.6302 | -0.7973
96102 | KRPH132 132.00 | KRPH | T1 | 8 | MELAKA | 1 | TNB T | 1 | 10.5963 | 0.116
96102 | KRPH132 132.00 | KRPH | T2 | 8 | MELAKA | 1 | TNB T | 1 | 11.9973 | 0.4277
96405 | MCOP132 132.00 | MCOP | T1 | 8 | MELAKA | 1 | TNB T | 1 | 13.2057 | 2.0234
96405 | MCOP132 132.00 | MCOP | T2 | 8 | MELAKA | 1 | TNB T | 1 | 10.4834 | 0.8294
96405 | MCOP132 132.00 | MCOP | T3 | 8 | MELAKA | 1 | TNB T | 1 | 37.6735 | -0.5416
96405 | MCOP132 132.00 | MCOP | T4 | 8 | MELAKA | 1 | TNB T | 1 | 37.7336 | -0.6762
96198 | MFDR132 132.00 | MFDR | F1 | 8 | MELAKA | 1 | TNB T | 1 | 0 | 0
96120 | MJYA132 132.00 | MJYA | T1 | 8 | MELAKA | 1 | TNB T | 1 | 5.6155 | 0.8636
96120 | MJYA132 132.00 | MJYA | T2 | 8 | MELAKA | 1 | TNB T | 1 | 16.3764 | 1.7044
96121 | MMAU132 132.00 | MMAU | T1 | 8 | MELAKA | 1 | TNB T | 1 | 12.2479 | 0.5312
96121 | MMAU132 132.00 | MMAU | T2 | 8 | MELAKA | 1 | TNB T | 1 | 10.8727 | 0.5457
96108 | MMKA132 132.00 | MMKA | T1 | 8 | MELAKA | 1 | TNB T | 1 | 9.3723 | 2.8455
96108 | MMKA132 132.00 | MMKA | T2 | 8 | MELAKA | 1 | TNB T | 1 | 7.0093 | 1.9395
96177 | MPSS132 132.00 | MPSS | T1 | 8 | MELAKA | 1 | TNB T | 1 | 2.9429 | 0.3189
96177 | MPSS132 132.00 | MPSS | T2 | 8 | MELAKA | 1 | TNB T | 1 | 6.0121 | 0.7352
96173 | MTNH132 132.00 | MTNH | T1 | 8 | MELAKA | 1 | TNB T | 1 | 6.2285 | 0.6555
96173 | MTNH132 132.00 | MTNH | T2 | 8 | MELAKA | 1 | TNB T | 1 | 6.2451 | 0.6027
96173 | MTNH132 132.00 | MTNH | T3 | 8 | MELAKA | 1 | TNB T | 1 | 2.8093 | 0.2817
96173 | MTNH132 132.00 | MTNH | T5 | 8 | MELAKA | 1 | TNB T | 1 | 11.3801 | -0.8284
96173 | MTNH132 132.00 | MTNH | T6 | 8 | MELAKA | 1 | TNB T | 1 | 11.4733 | -0.8491
196105 | OZNA132 132.00 | OZNA | T1 | 8 | MELAKA | 1 | TNB T | 1 | 8.5563 | -2.1542
196105 | OZNA132 132.00 | OZNA | T2 | 8 | MELAKA | 1 | TNB T | 1 | 8.5563 | -2.1542
96123 | PGAD132 132.00 | PGAD | T1 | 8 | MELAKA | 1 | TNB T | 1 | 20.8052 | -0.5964
96123 | PGAD132 132.00 | PGAD | T2 | 8 | MELAKA | 1 | TNB T | 1 | 20.886 | -0.6265
96147 | PPJG132 132.00 | PPJG | T1 | 8 | MELAKA | 1 | TNB T | 1 | 0 | 0
96147 | PPJG132 132.00 | PPJG | T2 | 8 | MELAKA | 1 | TNB T | 1 | 10.589 | 0.2268
96189 | TGBU132 132.00 | TGBU | T1 | 8 | MELAKA | 1 | TNB T | 1 | 3.7268 | 0.5851
96189 | TGBU132 132.00 | TGBU | T2 | 8 | MELAKA | 1 | TNB T | 1 | 3.6387 | 0.5509
96189 | TGBU132 132.00 | TGBU | T3 | 8 | MELAKA | 1 | TNB T | 1 | 16.7823 | 4.9807
96189 | TGBU132 132.00 | TGBU | T4 | 8 | MELAKA | 1 | TNB T | 1 | 16.861 | 4.9973
97117 | TKID132 132.00 | TKID | T1 | 8 | MELAKA | 1 | TNB T | 1 | 8.4725 | 0.5354
97117 | TKID132 132.00 | TKID | T2 | 8 | MELAKA | 1 | TNB T | 1 | 8.3958 | 0.5416
96110 | TMAS132 132.00 | TMAS | T1 | 8 | MELAKA | 1 | TNB T | 1 | 12.9779 | 1.2385
96110 | TMAS132 132.00 | TMAS | T2 | 8 | MELAKA | 1 | TNB T | 1 | 15.1711 | 1.5211
96113 | UPSR132 132.00 | UPSR | T1 | 8 | MELAKA | 1 | TNB T | 1 | 7.2423 | 0.6172
96113 | UPSR132 132.00 | UPSR | T2 | 8 | MELAKA | 1 | TNB T | 1 | 11.6318 | 1.0862
96113 | UPSR132 132.00 | UPSR | T3 | 8 | MELAKA | 1 | TNB T | 1 | 25.6545 | 3.4472
96113 | UPSR132 132.00 | UPSR | T4 | 8 | MELAKA | 1 | TNB T | 1 | 25.6421 | 3.3778
96195 | ZRNA132 132.00 | ZRNA | T1 | 8 | MELAKA | 1 | TNB T | 1 | 6.7297 | 0.4991
96195 | ZRNA132 132.00 | ZRNA | T2 | 8 | MELAKA | 1 | TNB T | 1 | 6.7473 | 0.5219
97122 | AHMJ132 132.00 | AHMJ | T1 | 9 | JOHOR | 1 | TNB T | 1 | 12.0325 | 0.963
97122 | AHMJ132 132.00 | AHMJ | T2 | 9 | JOHOR | 1 | TNB T | 1 | 12.1681 | -0.2402
97164 | BBTU132 132.00 | BBTU | T1 | 9 | JOHOR | 1 | TNB T | 1 | 12.747 | 2.4127
97164 | BBTU132 132.00 | BBTU | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.6597 | 0.9112
297111 | BBTU132_T7 132.00 | BBTU | T7 | 9 | JOHOR | 1 | TNB T | 1 | 8.5056 | 2.2015
97174 | BKPG132 132.00 | BKPG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 3.8365 | -0.7601
97174 | BKPG132 132.00 | BKPG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 3.8427 | -0.8118
97102 | BKRI132 132.00 | BKRI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 9.1735 | 2.8497
97102 | BKRI132 132.00 | BKRI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.6757 | -1.108
97106 | BPHE132 132.00 | BPHE | T1 | 9 | JOHOR | 40 | CAPACITORS | 1 | 34.9874 | 2.6706
97106 | BPHE132 132.00 | BPHE | T2 | 9 | JOHOR | 40 | CAPACITORS | 1 | 34.8942 | 2.6529
97129 | BPHT132 132.00 | BPHT | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.055 | 2.3423
97129 | BPHT132 132.00 | BPHT | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.8906 | 2.6157
97182 | BSPT132 132.00 | BSPT | T1 | 9 | JOHOR | 1 | TNB T | 1 | 9.7761 | 1.4321
97182 | BSPT132 132.00 | BSPT | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.7906 | 1.4145
97182 | BSPT132 132.00 | BSPT | T3 | 9 | JOHOR | 1 | TNB T | 1 | 15.3606 | -1.6112
97182 | BSPT132 132.00 | BSPT | T4 | 9 | JOHOR | 1 | TNB T | 1 | 15.5418 | -1.6216
97148 | CAAH132 132.00 | CAAH | T3 | 9 | JOHOR | 1 | TNB T | 1 | 9.9708 | 0.8615
97148 | CAAH132 132.00 | CAAH | T4 | 9 | JOHOR | 1 | TNB T | 1 | 9.9108 | 0.8615
97178 | CBRU132 132.00 | CBRU | T1 | 9 | JOHOR | 1 | TNB T | 1 | 8.9871 | 0.4701
97178 | CBRU132 132.00 | CBRU | T2 | 9 | JOHOR | 1 | TNB T | 1 | 8.9519 | 0.4567
97178 | CBRU132 132.00 | CBRU | T3 | 9 | JOHOR | 1 | TNB T | 1 | 24.7029 | -0.1595
97178 | CBRU132 132.00 | CBRU | T4 | 9 | JOHOR | 1 | TNB T | 1 | 24.4833 | -0.1595
97197 | DBAY132 132.00 | DBAY | T1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97197 | DBAY132 132.00 | DBAY | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97157 | DSRU132 132.00 | DSRU | T1 | 9 | JOHOR | 1 | TNB T | 1 | 4.4941 | -0.0932
97157 | DSRU132 132.00 | DSRU | T2 | 9 | JOHOR | 1 | TNB T | 1 | 6.4636 | -0.671
97176 | FCTR132 132.00 | FCTR | T1 | 9 | JOHOR | 1 | TNB T | 1 | 37.7853 | -6.7307
97176 | FCTR132 132.00 | FCTR | T2 | 9 | JOHOR | 1 | TNB T | 1 | 39.1211 | 3.8417
97187 | GPTH132 132.00 | GPTH | T1 | 9 | JOHOR | 1 | TNB T | 1 | 6.9482 | -0.0528
97187 | GPTH132 132.00 | GPTH | T2 | 9 | JOHOR | 1 | TNB T | 1 | 6.9182 | -0.0601
97187 | GPTH132 132.00 | GPTH | T3 | 9 | JOHOR | 40 | CAPACITORS | 1 | 38.5133 | -1.8763
97187 | GPTH132 132.00 | GPTH | T4 | 9 | JOHOR | 40 | CAPACITORS | 1 | 38.445 | -1.8556
97105 | GRSK132 132.00 | GRSK | T1 | 9 | JOHOR | 1 | TNB T | 1 | 12.0087 | 0.4049
97105 | GRSK132 132.00 | GRSK | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.9807 | 0.437
97253 | GSDC275 275.00 | GSDC | T1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97253 | GSDC275 275.00 | GSDC | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97253 | GSDC275 275.00 | GSDC | T3 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97253 | GSDC275 275.00 | GSDC | T4 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97407 | GWDC132 132.00 | GWDC | T1 | 9 | JOHOR | 1 | TNB T | 1 | 30.3815 | 7.0828
97407 | GWDC132 132.00 | GWDC | T2 | 9 | JOHOR | 1 | TNB T | 1 | 27.8963 | -5.4053
97194 | JBSK132 132.00 | JBSK | T1 | 9 | JOHOR | 1 | TNB T | 1 | 25.7425 | 1.9208
97194 | JBSK132 132.00 | JBSK | T2 | 9 | JOHOR | 1 | TNB T | 1 | 25.2548 | 1.8297
97150 | JMTH132 132.00 | JMTH | T1 | 9 | JOHOR | 1 | TNB T | 1 | 6.389 | -0.5509
97150 | JMTH132 132.00 | JMTH | T2 | 9 | JOHOR | 1 | TNB T | 1 | 7.5384 | -0.7311
97110 | JTGH132 132.00 | JTGH | T1 | 9 | JOHOR | 1 | TNB T | 1 | 12.193 | 1.7821
97110 | JTGH132 132.00 | JTGH | T2 | 9 | JOHOR | 1 | TNB T | 1 | 12.2458 | 1.779
97173 | KBEK132 132.00 | KBEK | T1 | 9 | JOHOR | 1 | TNB T | 1 | 0.232 | 4.9062
97173 | KBEK132 132.00 | KBEK | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0.8232 | 4.463
97168 | KKUP132 132.00 | KKUP | T1 | 9 | JOHOR | 1 | TNB T | 1 | 2.6664 | 0.0663
97168 | KKUP132 132.00 | KKUP | T2 | 9 | JOHOR | 1 | TNB T | 1 | 4.6753 | -0.1709
97112 | KLAI132 132.00 | KLAI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
597112 | KLAI132R 132.00 | KLAI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 20.1353 | 3.7765
97149 | KLID132 132.00 | KLID | T1 | 9 | JOHOR | 1 | TNB T | 1 | 10.1261 | 1.4124
97149 | KLID132 132.00 | KLID | T2 | 9 | JOHOR | 1 | TNB T | 1 | 10.852 | 0.2454
97149 | KLID132 132.00 | KLID | T3 | 9 | JOHOR | 1 | TNB T | 1 | 6.3331 | -0.0238
97149 | KLID132 132.00 | KLID | T4 | 9 | JOHOR | 1 | TNB T | 1 | 10.1158 | 2.2305
97109 | KLUG132 132.00 | KLUG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 8.5646 | 2.2936
97109 | KLUG132 132.00 | KLUG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 8.2529 | -0.9112
97109 | KLUG132 132.00 | KLUG | T3 | 9 | JOHOR | 1 | TNB T | 1 | 12.4208 | -2.0058
97109 | KLUG132 132.00 | KLUG | T4 | 9 | JOHOR | 1 | TNB T | 1 | 12.4125 | -1.9964
97132 | KPTR132 132.00 | KPTR | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.7539 | 0.7559
97132 | KPTR132 132.00 | KPTR | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.7488 | 0.7601
97158 | KSNI132 132.00 | KSNI | F1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97158 | KSNI132 132.00 | KSNI | F2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97189 | KTBR132 132.00 | KTBR | T1 | 9 | JOHOR | 1 | TNB T | 1 | 10.2173 | -0.2672
97189 | KTBR132 132.00 | KTBR | T2 | 9 | JOHOR | 1 | TNB T | 1 | 10.7071 | 3.7692
97189 | KTBR132 132.00 | KTBR | T3 | 9 | JOHOR | 40 | CAPACITORS | 1 | 33.488 | 1.6982
97189 | KTBR132 132.00 | KTBR | T4 | 9 | JOHOR | 40 | CAPACITORS | 1 | 33.0324 | 1.7603
97189 | KTBR132 132.00 | KTBR | T5 | 9 | JOHOR | 40 | CAPACITORS | 1 | 5.8599 | 0.2185
97189 | KTBR132 132.00 | KTBR | T6 | 9 | JOHOR | 40 | CAPACITORS | 1 | 5.7791 | 1.6993
97249 | KTDC275 275.00 | KTDC | T1 | 9 | JOHOR | 1 | TNB T | 1 | 28.0517 | -2.5732
97249 | KTDC275 275.00 | KTDC | T2 | 9 | JOHOR | 1 | TNB T | 1 | 22.9052 | 4.4578
97116 | KTGI132 132.00 | KTGI | T3 | 9 | JOHOR | 1 | TNB T | 1 | 8.3233 | 0.4919
97116 | KTGI132 132.00 | KTGI | T4 | 9 | JOHOR | 1 | TNB T | 1 | 5.8112 | 0.262
97185 | LKIN132 132.00 | LKIN | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.7415 | -0.1822
97185 | LKIN132 132.00 | LKIN | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.7995 | -0.1709
97185 | LKIN132 132.00 | LKIN | T3 | 9 | JOHOR | 1 | TNB T | 1 | 14.206 | 0.5467
97185 | LKIN132 132.00 | LKIN | T4 | 9 | JOHOR | 1 | TNB T | 1 | 14.1263 | 0.5467
97115 | MAJD132 132.00 | MAJD | T1 | 9 | JOHOR | 1 | TNB T | 1 | 6.5547 | -0.0466
97115 | MAJD132 132.00 | MAJD | T2 | 9 | JOHOR | 1 | TNB T | 1 | 6.2513 | -0.0549
97140 | MKBL132 132.00 | MKBL | T1 | 9 | JOHOR | 1 | TNB T | 1 | 5.6528 | 0.5768
97140 | MKBL132 132.00 | MKBL | T2 | 9 | JOHOR | 1 | TNB T | 1 | 15.2519 | 2.2118
97136 | MSAI132 132.00 | MSAI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.7995 | 1.5408
97136 | MSAI132 132.00 | MSAI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.7798 | 1.5305
97131 | MSNG132 132.00 | MSNG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 2.8311 | -4.667
97131 | MSNG132 132.00 | MSNG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 3.8686 | 4.2021
97131 | MSNG132 132.00 | MSNG | T3 | 9 | JOHOR | 1 | TNB T | 1 | 6.8384 | -1.5709
97131 | MSNG132 132.00 | MSNG | T4 | 9 | JOHOR | 1 | TNB T | 1 | 6.8291 | -1.5802
97147 | MUAR132 132.00 | MUAR | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.4168 | 1.5729
97147 | MUAR132 132.00 | MUAR | T3 | 9 | JOHOR | 1 | TNB T | 1 | 12.6041 | 1.4435
97138 | NYOR132 132.00 | NYOR | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.3926 | 0.4049
97138 | NYOR132 132.00 | NYOR | T2 | 9 | JOHOR | 1 | TNB T | 1 | 16.6104 | 3.208
97177 | PBJB132 132.00 | PBJB | T1 | 9 | JOHOR | 1 | TNB T | 1 | 9.6229 | 1.1214
97177 | PBJB132 132.00 | PBJB | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.6198 | 1.1183
97177 | PBJB132 132.00 | PBJB | T3 | 9 | JOHOR | 1 | TNB T | 1 | 43.0716 | 3.6543
97177 | PBJB132 132.00 | PBJB | T4 | 9 | JOHOR | 1 | TNB T | 1 | 43.2466 | 3.6408
97244 | PCGP275 275.00 | PCGP | 1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97153 | PGDT132 132.00 | PGDT | T1 | 9 | JOHOR | 1 | TNB T | 1 | 2.4873 | 0.0269
97153 | PGDT132 132.00 | PGDT | T2 | 9 | JOHOR | 1 | TNB T | 1 | 10.1427 | 2.4842
97153 | PGDT132 132.00 | PGDT | T3 | 9 | JOHOR | 40 | CAPACITORS | 1 | 16.3681 | 4.4123
97153 | PGDT132 132.00 | PGDT | T4 | 9 | JOHOR | 40 | CAPACITORS | 1 | 16.4624 | 4.4516
97191 | PGEH132 132.00 | PGEH | T1 | 9 | JOHOR | 1 | TNB T | 1 | 2.0379 | -0.378
97191 | PGEH132 132.00 | PGEH | T2 | 9 | JOHOR | 1 | TNB T | 1 | 2.0275 | -0.3676
97123 | PGIE132 132.00 | PGIE | T1 | 9 | JOHOR | 1 | TNB T | 1 | 13.8622 | 1.9882
97123 | PGIE132 132.00 | PGIE | T2 | 9 | JOHOR | 1 | TNB T | 1 | 13.8715 | 1.9861
97123 | PGIE132 132.00 | PGIE | T3 | 9 | JOHOR | 1 | TNB T | 1 | 12.4343 | 1.3068
97179 | PGOH132 132.00 | PGOH | T1 | 9 | JOHOR | 1 | TNB T | 1 | 3.4762 | -0.5033
97179 | PGOH132 132.00 | PGOH | T2 | 9 | JOHOR | 1 | TNB T | 1 | 3.4658 | -0.5136
97114 | PGPS132 132.00 | PGPS | N1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97114 | PGPS132 132.00 | PGPS | N2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97114 | PGPS132 132.00 | PGPS | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97167 | PGTC132 132.00 | PGTC | T1 | 9 | JOHOR | 1 | TNB T | 1 | 47.8349 | 11.9766
97167 | PGTC132 132.00 | PGTC | T2 | 9 | JOHOR | 1 | TNB T | 1 | 47.6754 | 11.9393
97103 | PJML132 132.00 | PJML | T3 | 9 | JOHOR | 1 | TNB T | 1 | 9.6156 | 0.6006
97103 | PJML132 132.00 | PJML | T4 | 9 | JOHOR | 1 | TNB T | 1 | 9.5804 | 0.5892
97198 | PLGI132 132.00 | PLGI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 29.0561 | 0.4577
97198 | PLGI132 132.00 | PLGI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 29.2052 | 0.4473
97108 | PLNG132 132.00 | PLNG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.4568 | 1.8639
97108 | PLNG132 132.00 | PLNG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.2983 | 1.5419
97108 | PLNG132 132.00 | PLNG | T3 | 9 | JOHOR | 1 | TNB T | 1 | 41.8124 | 2.5349
97108 | PLNG132 132.00 | PLNG | T4 | 9 | JOHOR | 1 | TNB T | 1 | 42.6677 | 2.5711
97165 | PMJY132 132.00 | PMJY | T1 | 9 | JOHOR | 1 | TNB T | 1 | 10.4844 | 1.7407
97165 | PMJY132 132.00 | PMJY | T2 | 9 | JOHOR | 1 | TNB T | 1 | 13.0918 | 0.9713
97165 | PMJY132 132.00 | PMJY | T3 | 9 | JOHOR | 1 | TNB T | 1 | 35.9556 | 1.4808
97165 | PMJY132 132.00 | PMJY | T4 | 9 | JOHOR | 1 | TNB T | 1 | 38.0297 | 1.4248
97155 | PNAS132 132.00 | PNAS | T1 | 9 | JOHOR | 1 | TNB T | 1 | 12.2686 | 2.3257
97155 | PNAS132 132.00 | PNAS | T2 | 9 | JOHOR | 1 | TNB T | 1 | 16.2076 | 3.326
97145 | PNWR132 132.00 | PNWR | T1 | 9 | JOHOR | 1 | TNB T | 1 | 6.2544 | 0.0342
97145 | PNWR132 132.00 | PNWR | T2 | 9 | JOHOR | 1 | TNB T | 1 | 5.162 | -0.0104
97151 | PONT132 132.00 | PONT | T1 | 9 | JOHOR | 1 | TNB T | 1 | 6.5195 | -0.233
97151 | PONT132 132.00 | PONT | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.2538 | 2.0731
97151 | PONT132 132.00 | PONT | T3 | 9 | JOHOR | 1 | TNB T | 1 | 12.456 | 0.5964
97151 | PONT132 132.00 | PONT | T4 | 9 | JOHOR | 1 | TNB T | 1 | 12.4829 | 0.3024
97119 | PRJA132 132.00 | PRJA | T1 | 9 | JOHOR | 1 | TNB T | 1 | 20.4677 | 4.5634
97119 | PRJA132 132.00 | PRJA | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97119 | PRJA132 132.00 | PRJA | T3 | 9 | JOHOR | 1 | TNB T | 1 | 1.2457 | 0.117
97119 | PRJA132 132.00 | PRJA | T4 | 9 | JOHOR | 1 | TNB T | 1 | 1.2571 | 0.1263
97163 | PSAK132 132.00 | PSAK | T1 | 9 | JOHOR | 1 | TNB T | 1 | 7.9858 | -0.1936
97163 | PSAK132 132.00 | PSAK | T2 | 9 | JOHOR | 1 | TNB T | 1 | 16.4748 | 0.2423
97163 | PSAK132 132.00 | PSAK | T3 | 9 | JOHOR | 1 | TNB T | 1 | 11.9331 | -7.6047
97163 | PSAK132 132.00 | PSAK | T4 | 9 | JOHOR | 1 | TNB T | 1 | 12.0263 | -7.6917
97181 | PSLG132 132.00 | PSLG | T3 | 9 | JOHOR | 1 | TNB T | 1 | 6.4667 | 0.0538
97181 | PSLG132 132.00 | PSLG | T4 | 9 | JOHOR | 1 | TNB T | 1 | 7.497 | -1.1939
97120 | PSRI132 132.00 | PSRI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 6.8032 | 0.9361
97120 | PSRI132 132.00 | PSRI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 16.16 | 1.6765
97118 | PUBB132 132.00 | PUBB | T1 | 9 | JOHOR | 1 | TNB T | 1 | 10.1582 | 2.363
97118 | PUBB132 132.00 | PUBB | T2 | 9 | JOHOR | 1 | TNB T | 1 | 10.2514 | 2.3806
97104 | PYSF132 132.00 | PYSF | T1 | 9 | JOHOR | 1 | TNB T | 1 | 4.0208 | -0.0859
97104 | PYSF132 132.00 | PYSF | T2 | 9 | JOHOR | 1 | TNB T | 1 | 3.9867 | -0.0859
97111 | RNGM132 132.00 | RNGM | T1 | 9 | JOHOR | 1 | TNB T | 1 | 4.3905 | -1.7086
97111 | RNGM132 132.00 | RNGM | T2 | 9 | JOHOR | 1 | TNB T | 1 | 4.4765 | 0.8978
97124 | RNGT132 132.00 | RNGT | T1 | 9 | JOHOR | 1 | TNB T | 1 | 7.9526 | -0.1232
97124 | RNGT132 132.00 | RNGT | T2 | 9 | JOHOR | 1 | TNB T | 1 | 6.7204 | -0.1553
97124 | RNGT132 132.00 | RNGT | T3 | 9 | JOHOR | 1 | TNB T | 1 | 9.0824 | -0.1988
97134 | SABG132 132.00 | SABG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 10.094 | 0.8926
97134 | SABG132 132.00 | SABG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.085 | 1.5243
97134 | SABG132 132.00 | SABG | T3 | 9 | JOHOR | 1 | TNB T | 1 | 27.6737 | 2.5214
97134 | SABG132 132.00 | SABG | T4 | 9 | JOHOR | 1 | TNB T | 1 | 27.331 | 2.4779
97113 | SDAI132 132.00 | SDAI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 30.0191 | 3.1148
97113 | SDAI132 132.00 | SDAI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 29.783 | 3.0216
97113 | SDAI132 132.00 | SDAI | T7 | 9 | JOHOR | 1 | TNB T | 1 | 0.6275 | -0.3334
97113 | SDAI132 132.00 | SDAI | T8 | 9 | JOHOR | 1 | TNB T | 1 | 0.6741 | -0.3106
197113 | SDAI132_T9 132.00 | SDAI | T9 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97137 | SDNK132 132.00 | SDNK | T1 | 9 | JOHOR | 1 | TNB T | 1 | 2.7731 | -0.3179
97137 | SDNK132 132.00 | SDNK | T2 | 9 | JOHOR | 1 | TNB T | 1 | 2.7741 | -0.3272
97142 | SELG132 132.00 | SELG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97142 | SELG132 132.00 | SELG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 14.6927 | 1.7396
97146 | SGAD132 132.00 | SGAD | T1 | 9 | JOHOR | 1 | TNB T | 1 | 15.2177 | 3.8521
97146 | SGAD132 132.00 | SGAD | T2 | 9 | JOHOR | 1 | TNB T | 1 | 8.7023 | 2.3692
97146 | SGAD132 132.00 | SGAD | T3 | 9 | JOHOR | 1 | TNB T | 1 | 11.9062 | 2.1704
97146 | SGAD132 132.00 | SGAD | T4 | 9 | JOHOR | 1 | TNB T | 1 | 10.7537 | 2.8466
97141 | SGMT132 132.00 | SGMT | T1 | 9 | JOHOR | 1 | TNB T | 1 | 7.9878 | -0.3169
97141 | SGMT132 132.00 | SGMT | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.8466 | 0.2848
97126 | SHTE132 132.00 | SHTE | T1 | 9 | JOHOR | 1 | TNB T | 1 | 33.749 | -0.2775
97126 | SHTE132 132.00 | SHTE | T2 | 9 | JOHOR | 1 | TNB T | 1 | 33.5108 | -0.2682
97251 | SIDC275 275.00 | SIDC | T1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97251 | SIDC275 275.00 | SIDC | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97190 | SKRG132 132.00 | SKRG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 2.1176 | 0.5467
597190 | SKRG132R 132.00 | SKRG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 2.3754 | 0.2982
97143 | SLNG132 132.00 | SLNG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 12.4767 | 1.8328
97143 | SLNG132 132.00 | SLNG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 13.5661 | 2.7969
97143 | SLNG132 132.00 | SLNG | T3 | 9 | JOHOR | 1 | TNB T | 1 | 29.1514 | -2.1828
97143 | SLNG132 132.00 | SLNG | T4 | 9 | JOHOR | 1 | TNB T | 1 | 29.0064 | 9.0761
97154 | SMTI132 132.00 | SMTI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 9.2491 | 0.3376
97154 | SMTI132 132.00 | SMTI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.509 | 0.4929
97154 | SMTI132 132.00 | SMTI | T3 | 9 | JOHOR | 1 | TNB T | 1 | 6.9233 | -1.7272
97154 | SMTI132 132.00 | SMTI | T4 | 9 | JOHOR | 1 | TNB T | 1 | 7.1253 | -1.78
97162 | SNAI132 132.00 | SNAI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 9.6219 | 2.6022
97162 | SNAI132 132.00 | SNAI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.6229 | 2.6063
97162 | SNAI132 132.00 | SNAI | T3 | 9 | JOHOR | 1 | TNB T | 1 | 43.0695 | 7.0362
97162 | SNAI132 132.00 | SNAI | T4 | 9 | JOHOR | 40 | CAPACITORS | 1 | 42.6719 | 6.9658
96115 | SRBI132 132.00 | SRBI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 6.2078 | -2.2916
96115 | SRBI132 132.00 | SRBI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 6.2182 | -2.2812
97139 | SRGM132 132.00 | SRGM | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.8295 | 0.3759
97139 | SRGM132 132.00 | SRGM | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.1435 | 1.0303
97125 | SSLG132 132.00 | SSLG | T3 | 9 | JOHOR | 1 | TNB T | 1 | 4.5013 | 0.3893
97125 | SSLG132 132.00 | SSLG | T4 | 9 | JOHOR | 1 | TNB T | 1 | 4.5106 | 0.3987
97254 | STDC275 275.00 | STDC | T1 | 9 | JOHOR | 1 | TNB T | 1 | 2.189 | 3.4482
97254 | STDC275 275.00 | STDC | T2 | 9 | JOHOR | 1 | TNB T | 1 | 2.189 | 3.4482
97254 | STDC275 275.00 | STDC | T3 | 9 | JOHOR | 1 | TNB T | 1 | 2.189 | 3.4482
97254 | STDC275 275.00 | STDC | T4 | 9 | JOHOR | 1 | TNB T | 1 | 2.189 | 3.4482
97152 | STUL132 132.00 | STUL | T1 | 9 | JOHOR | 1 | TNB T | 1 | 5.2914 | 0.057
97152 | STUL132 132.00 | STUL | T2 | 9 | JOHOR | 1 | TNB T | 1 | 5.2779 | 0.0621
97101 | TAGS132 132.00 | TAGS | T1 | 9 | JOHOR | 1 | TNB T | 1 | 6.2938 | 0.6006
97101 | TAGS132 132.00 | TAGS | T2 | 9 | JOHOR | 1 | TNB T | 1 | 12.2655 | 2.8424
97135 | TBKR132 132.00 | TBKR | T1 | 9 | JOHOR | 1 | TNB T | 1 | 0.6762 | -0.1574
97135 | TBKR132 132.00 | TBKR | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0.6834 | -0.1626
97186 | TBRU132 132.00 | TBRU | T1 | 9 | JOHOR | 1 | TNB T | 1 | 23.2293 | 3.4524
97186 | TBRU132 132.00 | TBRU | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97186 | TBRU132 132.00 | TBRU | T3 | 9 | JOHOR | 1 | TNB T | 1 | 40.3223 | 7.2361
97186 | TBRU132 132.00 | TBRU | T4 | 9 | JOHOR | 1 | TNB T | 1 | 39.614 | 7.0207
97128 | TKAK132 132.00 | TKAK | T3 | 9 | JOHOR | 1 | TNB T | 1 | 11.1461 | -0.787
97128 | TKAK132 132.00 | TKAK | T4 | 9 | JOHOR | 1 | TNB T | 1 | 11.2041 | -0.7849
97166 | TKPG132 132.00 | TKPG | T1 | 9 | JOHOR | 1 | TNB T | 1 | 5.6683 | 1.2385
97166 | TKPG132 132.00 | TKPG | T2 | 9 | JOHOR | 1 | TNB T | 1 | 5.9603 | 1.4311
97166 | TKPG132 132.00 | TKPG | T3 | 9 | JOHOR | 1 | TNB T | 1 | 15.0562 | -2.8114
97166 | TKPG132 132.00 | TKPG | T4 | 9 | JOHOR | 1 | TNB T | 1 | 15.0147 | -2.7793
97180 | TLBH132 132.00 | TLBH | T1 | 9 | JOHOR | 1 | TNB T | 1 | 12.6745 | 1.8328
97180 | TLBH132 132.00 | TLBH | T2 | 9 | JOHOR | 1 | TNB T | 1 | 12.2738 | 0.379
97184 | TLST132 132.00 | TLST | T1 | 9 | JOHOR | 1 | TNB T | 1 | 8.429 | -0.262
97184 | TLST132 132.00 | TLST | T2 | 9 | JOHOR | 1 | TNB T | 1 | 8.4507 | -0.2516
97184 | TLST132 132.00 | TLST | T3 | 9 | JOHOR | 1 | TNB T | 1 | 8.8701 | 0.8812
97184 | TLST132 132.00 | TLST | T4 | 9 | JOHOR | 1 | TNB T | 1 | 8.5304 | 1.4103
97184 | TLST132 132.00 | TLST | T5 | 9 | JOHOR | 1 | TNB T | 1 | 24.6884 | 0.3717
97184 | TLST132 132.00 | TLST | T6 | 9 | JOHOR | 1 | TNB T | 1 | 24.6832 | 0.4038
97192 | TMPI132 132.00 | TMPI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 29.0913 | 10.005
97192 | TMPI132 132.00 | TMPI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 27.9139 | -1.9229
97121 | TPCH132 132.00 | TPCH | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.4329 | 1.1711
97121 | TPCH132 132.00 | TPCH | T2 | 9 | JOHOR | 1 | TNB T | 1 | 4.8668 | 0.4442
97127 | TPOI132 132.00 | TPOI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.9093 | -0.4235
97127 | TPOI132 132.00 | TPOI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 11.9165 | -0.4101
97130 | TRMN132 132.00 | TRMN | T1 | 9 | JOHOR | 1 | TNB T | 1 | 2.4345 | -0.4287
97130 | TRMN132 132.00 | TRMN | T2 | 9 | JOHOR | 1 | TNB T | 1 | 2.4096 | -0.4318
97130 | TRMN132 132.00 | TRMN | T3 | 9 | JOHOR | 1 | TNB T | 1 | 7.3655 | -0.875
97130 | TRMN132 132.00 | TRMN | T4 | 9 | JOHOR | 1 | TNB T | 1 | 6.8788 | -10.7754
97144 | TTKJ132 132.00 | TTKJ | T1 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97144 | TTKJ132 132.00 | TTKJ | T2 | 9 | JOHOR | 1 | TNB T | 1 | 0 | 0
97195 | TUNI132 132.00 | TUNI | T1 | 9 | JOHOR | 1 | TNB T | 1 | 11.5821 | 1.2188
97195 | TUNI132 132.00 | TUNI | T2 | 9 | JOHOR | 1 | TNB T | 1 | 18.0301 | 2.9905
97188 | UTRM132 132.00 | UTRM | T1 | 9 | JOHOR | 1 | TNB T | 1 | 9.2791 | 0.2558
97188 | UTRM132 132.00 | UTRM | T2 | 9 | JOHOR | 1 | TNB T | 1 | 9.3102 | 0.233
97188 | UTRM132 132.00 | UTRM | T3 | 9 | JOHOR | 1 | TNB T | 1 | 30.5555 | 2.6706
97188 | UTRM132 132.00 | UTRM | T4 | 9 | JOHOR | 1 | TNB T | 1 | 29.6836 | 2.5546
97107 | YGPG132 132.00 | YGPG | T1 | 9 | JOHOR | 40 | CAPACITORS | 1 | 11.4443 | 0.6348
97107 | YGPG132 132.00 | YGPG | T2 | 9 | JOHOR | 40 | CAPACITORS | 1 | 9.8683 | -0.6575
97107 | YGPG132 132.00 | YGPG | T3 | 9 | JOHOR | 40 | CAPACITORS | 1 | 0 | 0
97107 | YGPG132 132.00 | YGPG | T4 | 9 | JOHOR | 40 | CAPACITORS | 1 | 11.0736 | 1.8142
74104 | ATNI132 132.00 | ATNI | T1 | 10 | PAHANG | 1 | TNB T | 1 | 3.5973 | -0.1885
74104 | ATNI132 132.00 | ATNI | T2 | 10 | PAHANG | 1 | TNB T | 1 | 4.1006 | 0.9112
74128 | BIMK132 132.00 | BIMK | T1 | 10 | PAHANG | 1 | TNB T | 1 | 10.0526 | 0.8315
74128 | BIMK132 132.00 | BIMK | T2 | 10 | PAHANG | 1 | TNB T | 1 | 11.2828 | 0.8325
74128 | BIMK132 132.00 | BIMK | T3 | 10 | PAHANG | 1 | TNB T | 1 | 37.4146 | 3.0143
74128 | BIMK132 132.00 | BIMK | T4 | 10 | PAHANG | 1 | TNB T | 1 | 37.6424 | 2.9957
74112 | BMSH132 132.00 | BMSH | T1 | 10 | PAHANG | 1 | TNB T | 1 | 11.959 | -2.3806
74112 | BMSH132 132.00 | BMSH | T2 | 10 | PAHANG | 1 | TNB T | 1 | 11.9041 | -2.391
74120 | BNTA132 132.00 | BNTA | T1 | 10 | PAHANG | 1 | TNB T | 1 | 2.7813 | -0.2485
74120 | BNTA132 132.00 | BNTA | T2 | 10 | PAHANG | 1 | TNB T | 1 | 2.7896 | -0.2578
74118 | BNTG132 132.00 | BNTG | T1 | 10 | PAHANG | 1 | TNB T | 1 | 8.081 | 0.8771
74118 | BNTG132 132.00 | BNTG | T2 | 10 | PAHANG | 1 | TNB T | 1 | 11.3387 | 1.9208
74101 | BTRT132 132.00 | BTRT | T1 | 10 | PAHANG | 1 | TNB T | 1 | 0.5457 | -0.1874
74101 | BTRT132 132.00 | BTRT | T2 | 10 | PAHANG | 1 | TNB T | 1 | 0.5478 | -0.1854
74150 | CUFG132 132.00 | CUFG | 99 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74137 | GBID132 132.00 | GBID | T1 | 10 | PAHANG | 1 | TNB T | 1 | 22.3958 | -0.3438
74137 | GBID132 132.00 | GBID | T2 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74138 | GBNG132 132.00 | GBNG | T1 | 10 | PAHANG | 1 | TNB T | 1 | 2.7917 | 0.5478
74138 | GBNG132 132.00 | GBNG | T2 | 10 | PAHANG | 1 | TNB T | 1 | 7.7517 | 1.3089
74138 | GBNG132 132.00 | GBNG | T3 | 10 | PAHANG | 40 | CAPACITORS | 1 | 12.6144 | 0.7062
74138 | GBNG132 132.00 | GBNG | T4 | 10 | PAHANG | 40 | CAPACITORS | 1 | 12.4167 | 0.6959
74125 | GTNG132 132.00 | GTNG | T1 | 10 | PAHANG | 1 | TNB T | 1 | 1.0024 | -0.0228
74125 | GTNG132 132.00 | GTNG | T2 | 10 | PAHANG | 1 | TNB T | 1 | 5.9552 | 0.4256
74135 | JBRS132 132.00 | JBRS | T1 | 10 | PAHANG | 1 | TNB T | 1 | 9.0151 | -0.8243
74135 | JBRS132 132.00 | JBRS | T2 | 10 | PAHANG | 1 | TNB T | 1 | 7.8035 | -1.3907
74135 | JBRS132 132.00 | JBRS | T3 | 10 | PAHANG | 1 | TNB T | 1 | 4.1958 | -0.9837
74135 | JBRS132 132.00 | JBRS | T4 | 10 | PAHANG | 1 | TNB T | 1 | 4.1772 | -0.9817
74123 | JNKA132 132.00 | JNKA | T1 | 10 | PAHANG | 1 | TNB T | 1 | 12.5948 | 0.1108
74123 | JNKA132 132.00 | JNKA | T2 | 10 | PAHANG | 1 | TNB T | 1 | 12.6745 | 0.466
74123 | JNKA132 132.00 | JNKA | T7 | 10 | PAHANG | 1 | TNB T | 1 | 5.542 | -2.3899
74122 | JTUT132 132.00 | JTUT | T1 | 10 | PAHANG | 1 | TNB T | 1 | 19.1629 | -0.3417
74122 | JTUT132 132.00 | JTUT | T2 | 10 | PAHANG | 1 | TNB T | 1 | 18.9921 | -0.4225
74110 | KAWA132 132.00 | KAWA | T1 | 10 | PAHANG | 1 | TNB T | 1 | 9.2915 | 0.262
74110 | KAWA132 132.00 | KAWA | T2 | 10 | PAHANG | 1 | TNB T | 1 | 9.2025 | 0.2558
74121 | KLIP132 132.00 | KLIP | T1 | 10 | PAHANG | 1 | TNB T | 1 | 11.407 | 0.1771
74121 | KLIP132 132.00 | KLIP | T2 | 10 | PAHANG | 1 | TNB T | 1 | 5.9976 | 0.9837
74121 | KLIP132 132.00 | KLIP | T3 | 10 | PAHANG | 1 | TNB T | 1 | 12.9841 | -0.2734
74121 | KLIP132 132.00 | KLIP | T4 | 10 | PAHANG | 1 | TNB T | 1 | 12.4798 | -0.1999
74116 | KRAK132 132.00 | KRAK | T1 | 10 | PAHANG | 1 | TNB T | 1 | 2.0089 | -0.1149
74116 | KRAK132 132.00 | KRAK | T2 | 10 | PAHANG | 1 | TNB T | 1 | 1.6993 | -0.0683
74116 | KRAK132 132.00 | KRAK | T3 | 10 | PAHANG | 1 | TNB T | 1 | 3.0061 | -0.5364
74116 | KRAK132 132.00 | KRAK | T4 | 10 | PAHANG | 1 | TNB T | 1 | 2.9978 | -0.5385
74145 | KRYG132 132.00 | KRYG | T1 | 10 | PAHANG | 1 | TNB T | 1 | 31.6769 | -6.8446
74145 | KRYG132 132.00 | KRYG | T2 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74108 | KTAN132 132.00 | KTAN | T1 | 10 | PAHANG | 1 | TNB T | 1 | 15.1411 | 0.5033
74108 | KTAN132 132.00 | KTAN | T2 | 10 | PAHANG | 1 | TNB T | 1 | 15.7603 | 4.784
74108 | KTAN132 132.00 | KTAN | T3 | 10 | PAHANG | 1 | TNB T | 1 | 14.8553 | 1.9954
74108 | KTAN132 132.00 | KTAN | T4 | 10 | PAHANG | 1 | TNB T | 1 | 26.0345 | -0.7652
74108 | KTAN132 132.00 | KTAN | T5 | 10 | PAHANG | 1 | TNB T | 1 | 26.1349 | -0.7559
74141 | KTCL132 132.00 | KTCL | T1 | 10 | PAHANG | 1 | TNB T | 1 | 8.4994 | 3.9028
74141 | KTCL132 132.00 | KTCL | T2 | 10 | PAHANG | 1 | TNB T | 1 | 8.2198 | -0.116
74132 | KTRI132 132.00 | KTRI | T1 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74143 | MECC132 132.00 | MECC | T1 | 10 | PAHANG | 1 | TNB T | 1 | 6.8643 | -0.7663
74143 | MECC132 132.00 | MECC | T2 | 10 | PAHANG | 1 | TNB T | 1 | 6.9254 | -0.7746
74143 | MECC132 132.00 | MECC | T3 | 10 | PAHANG | 1 | TNB T | 1 | 0.9433 | 7.9754
74143 | MECC132 132.00 | MECC | T4 | 10 | PAHANG | 1 | TNB T | 1 | 0.9216 | 8.0448
74129 | MRAN132 132.00 | MRAN | T1 | 10 | PAHANG | 1 | TNB T | 1 | 4.493 | -1.0697
74129 | MRAN132 132.00 | MRAN | T2 | 10 | PAHANG | 1 | TNB T | 1 | 4.5531 | -1.0717
74117 | MTKB132 132.00 | MTKB | T1 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74117 | MTKB132 132.00 | MTKB | T2 | 10 | PAHANG | 1 | TNB T | 1 | 22.578 | 2.6457
74109 | PKAN132 132.00 | PKAN | T1 | 10 | PAHANG | 1 | TNB T | 1 | 4.6742 | 0.2516
74109 | PKAN132 132.00 | PKAN | T2 | 10 | PAHANG | 1 | TNB T | 1 | 4.6815 | 0.2547
74109 | PKAN132 132.00 | PKAN | T3 | 10 | PAHANG | 1 | TNB T | 1 | 6.3994 | 0.5281
74115 | PKNI132 132.00 | PKNI | T1 | 10 | PAHANG | 1 | TNB T | 1 | 6.2824 | -0.1398
74115 | PKNI132 132.00 | PKNI | T2 | 10 | PAHANG | 1 | TNB T | 1 | 6.3124 | -0.1491
174920 | PNLS132 132.00 | PNLS | T1 | 10 | PAHANG | 1 | TNB T | 1 | 0 | -0.7679
74151 | RBDR132 132.00 | RBDR | T1 | 10 | PAHANG | 1 | TNB T | 1 | 11.7011 | 0.0414
74151 | RBDR132 132.00 | RBDR | T2 | 10 | PAHANG | 1 | TNB T | 1 | 11.0332 | 0.2475
74151 | RBDR132 132.00 | RBDR | T3 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74151 | RBDR132 132.00 | RBDR | T4 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74107 | SMBU132 132.00 | SMBU | T1 | 10 | PAHANG | 1 | TNB T | 1 | 10.6066 | 0.9993
74107 | SMBU132 132.00 | SMBU | T2 | 10 | PAHANG | 1 | TNB T | 1 | 6.0825 | 0.6482
74127 | SONG132 132.00 | SONG | T1 | 10 | PAHANG | 1 | TNB T | 1 | 14.467 | 1.3068
74127 | SONG132 132.00 | SONG | T2 | 10 | PAHANG | 1 | TNB T | 1 | 7.612 | 0.408
74157 | TAGP132 132.00 | TAGP | T7 | 10 | PAHANG | 1 | TNB T | 1 | 3.5787 | 0.0445
74106 | TGLN132 132.00 | TGLN | T1 | 10 | PAHANG | 1 | TNB T | 1 | 5.9562 | 1.2623
74106 | TGLN132 132.00 | TGLN | T2 | 10 | PAHANG | 1 | TNB T | 1 | 5.2148 | 1.1919
74106 | TGLN132 132.00 | TGLN | T3 | 10 | PAHANG | 1 | TNB T | 1 | 11.2642 | 3.0071
74133 | TGMK132 132.00 | TGMK | T1 | 10 | PAHANG | 1 | TNB T | 1 | 13.7514 | -1.7914
74133 | TGMK132 132.00 | TGMK | T2 | 10 | PAHANG | 1 | TNB T | 1 | 13.7411 | -1.8018
74111 | TJBU132 132.00 | TJBU | T1 | 10 | PAHANG | 1 | TNB T | 1 | 2.1818 | -0.174
74111 | TJBU132 132.00 | TJBU | T2 | 10 | PAHANG | 1 | TNB T | 1 | 2.2211 | -0.1646
74144 | TMID132 132.00 | TMID | T1 | 10 | PAHANG | 1 | TNB T | 1 | 9.0399 | -0.5188
74144 | TMID132 132.00 | TMID | T2 | 10 | PAHANG | 1 | TNB T | 1 | 9.1155 | 3.4803
74144 | TMID132 132.00 | TMID | T3 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74144 | TMID132 132.00 | TMID | T4 | 10 | PAHANG | 1 | TNB T | 1 | 0 | 0
74156 | UIAM132 132.00 | UIAM | T1 | 10 | PAHANG | 1 | TNB T | 1 | 8.196 | -0.1315
74156 | UIAM132 132.00 | UIAM | T2 | 10 | PAHANG | 1 | TNB T | 1 | 8.197 | -0.1149
75138 | BRKT132 132.00 | BRKT | T1 | 11 | TGANU | 1 | TNB T | 1 | 9.1207 | -0.5757
75138 | BRKT132 132.00 | BRKT | T2 | 11 | TGANU | 1 | TNB T | 1 | 9.0182 | -0.5561
75138 | BRKT132 132.00 | BRKT | T3 | 11 | TGANU | 1 | TNB T | 1 | 14.7041 | 0.642
75109 | CHRG132 132.00 | CHRG | T1 | 11 | TGANU | 1 | TNB T | 1 | 17.8064 | 3.6367
75109 | CHRG132 132.00 | CHRG | T2 | 11 | TGANU | 1 | TNB T | 1 | 14.3209 | -0.1067
75109 | CHRG132 132.00 | CHRG | T3 | 11 | TGANU | 1 | TNB T | 1 | 25.6648 | -6.7442
75109 | CHRG132 132.00 | CHRG | T4 | 11 | TGANU | 1 | TNB T | 1 | 26.2426 | 6.2617
75144 | CKAI132 132.00 | CKAI | T1 | 11 | TGANU | 1 | TNB T | 1 | 12.7325 | 1.9674
75144 | CKAI132 132.00 | CKAI | T2 | 11 | TGANU | 1 | TNB T | 1 | 12.7594 | 1.9799
75150 | CUFK132 132.00 | CUFK | 99 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75118 | DGID132 132.00 | DGID | T1 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75118 | DGID132 132.00 | DGID | T2 | 11 | TGANU | 1 | TNB T | 1 | 25.8719 | -1.6848
75103 | DGUN132 132.00 | DGUN | T1 | 11 | TGANU | 1 | TNB T | 1 | 5.2179 | 0.1408
75103 | DGUN132 132.00 | DGUN | T2 | 11 | TGANU | 1 | TNB T | 1 | 5.1723 | 0.1512
75116 | GBDK132 132.00 | GBDK | T1 | 11 | TGANU | 1 | TNB T | 1 | 10.6625 | 1.2643
75116 | GBDK132 132.00 | GBDK | T2 | 11 | TGANU | 1 | TNB T | 1 | 10.6832 | 1.1846
75116 | GBDK132 132.00 | GBDK | T3 | 11 | TGANU | 1 | TNB T | 1 | 19.3752 | 0.1543
75116 | GBDK132 132.00 | GBDK | T4 | 11 | TGANU | 1 | TNB T | 1 | 19.4291 | 0.1885
75299 | HTRG275 275.00 | HTRG | T1 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75299 | HTRG275 275.00 | HTRG | T2 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75926 | HTRG_U3 11.000 | HTRG | X1 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75927 | HTRG_U4 11.000 | HTRG | X1 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75140 | KBRG132 132.00 | KBRG | T1 | 11 | TGANU | 1 | TNB T | 1 | 10.8862 | -0.5581
75140 | KBRG132 132.00 | KBRG | T2 | 11 | TGANU | 1 | TNB T | 1 | 10.4865 | -0.8201
75140 | KBRG132 132.00 | KBRG | T3 | 11 | TGANU | 1 | TNB T | 1 | 5.0563 | -4.5044
75140 | KBRG132 132.00 | KBRG | T4 | 11 | TGANU | 1 | TNB T | 1 | 5.133 | -4.6349
75105 | KMAN132 132.00 | KMAN | T1 | 11 | TGANU | 1 | TNB T | 1 | 9.656 | 1.3337
75105 | KMAN132 132.00 | KMAN | T2 | 11 | TGANU | 1 | TNB T | 1 | 9.685 | 1.3089
75105 | KMAN132 132.00 | KMAN | T3 | 11 | TGANU | 1 | TNB T | 1 | 2.858 | -2.8331
75105 | KMAN132 132.00 | KMAN | T4 | 11 | TGANU | 1 | TNB T | 1 | 2.8777 | -2.8279
75102 | KNYR132 132.00 | KNYR | T1 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75102 | KNYR132 132.00 | KNYR | T2 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75115 | KTGU132 132.00 | KTGU | T1 | 11 | TGANU | 1 | TNB T | 1 | 13.361 | 1.3896
75115 | KTGU132 132.00 | KTGU | T2 | 11 | TGANU | 1 | TNB T | 1 | 11.4909 | 1.2716
75115 | KTGU132 132.00 | KTGU | T3 | 11 | TGANU | 1 | TNB T | 1 | 11.521 | 1.7127
75115 | KTGU132 132.00 | KTGU | T4 | 11 | TGANU | 1 | TNB T | 1 | 11.5365 | 1.7262
75124 | KTIH132 132.00 | KTIH | T1 | 11 | TGANU | 1 | TNB T | 1 | 5.9676 | 0.9672
75124 | KTIH132 132.00 | KTIH | T2 | 11 | TGANU | 1 | TNB T | 1 | 5.9614 | 0.964
74261 | MCKP275 275.00 | MCKP | T1 | 11 | TGANU | 1 | TNB T | 1 | 0.5009 | -0.413
74261 | MCKP275 275.00 | MCKP | T2 | 11 | TGANU | 1 | TNB T | 1 | 0.5009 | -0.413
75910 | MCLS_LSS1 0.6000 | MCLS | X1 | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75104 | PAKA132 132.00 | PAKA | NA | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75104 | PAKA132 132.00 | PAKA | NB | 11 | TGANU | 1 | TNB T | 1 | 0 | 0
75104 | PAKA132 132.00 | PAKA | T1 | 11 | TGANU | 1 | TNB T | 1 | 6.6199 | 1.8908
75104 | PAKA132 132.00 | PAKA | T2 | 11 | TGANU | 1 | TNB T | 1 | 6.5992 | 1.7717
75104 | PAKA132 132.00 | PAKA | T5 | 11 | TGANU | 1 | TNB T | 1 | 2.4407 | 0.5354
75104 | PAKA132 132.00 | PAKA | T6 | 11 | TGANU | 1 | TNB T | 1 | 2.4065 | 0.5302
75111 | RPTS132 132.00 | RPTS | T1 | 11 | TGANU | 1 | TNB T | 1 | 6.4108 | 0.1574
75111 | RPTS132 132.00 | RPTS | T2 | 11 | TGANU | 1 | TNB T | 1 | 6.4046 | 0.1564
75120 | STNG132 132.00 | STNG | T1 | 11 | TGANU | 1 | TNB T | 1 | 6.4594 | -0.4888
75120 | STNG132 132.00 | STNG | T2 | 11 | TGANU | 1 | TNB T | 1 | 6.5205 | -0.4888
75126 | TKLG132 132.00 | TKLG | T1 | 11 | TGANU | 1 | TNB T | 1 | 3.6097 | -0.1874
75126 | TKLG132 132.00 | TKLG | T2 | 11 | TGANU | 1 | TNB T | 1 | 3.6087 | -0.1895
75126 | TKLG132 132.00 | TKLG | T3 | 11 | TGANU | 1 | TNB T | 1 | 18.7373 | 3.56
75126 | TKLG132 132.00 | TKLG | T4 | 11 | TGANU | 1 | TNB T | 1 | 18.7881 | 3.5507
75133 | GMSG132 132.00 | GMSG | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 5.9769 | 0.4991
75133 | GMSG132 132.00 | GMSG | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 5.9489 | 0.5012
75133 | GMSG132 132.00 | GMSG | T3 | 12 | KELANTAN | 1 | TNB T | 1 | 6.2378 | -1.0106
75133 | GMSG132 132.00 | GMSG | T4 | 12 | KELANTAN | 1 | TNB T | 1 | 6.2451 | -0.9972
75206 | JELI275 275.00 | JELI | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 6.3818 | -1.4559
75206 | JELI275 275.00 | JELI | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 6.1705 | -2.0824
75112 | KBRU132 132.00 | KBRU | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 25.5758 | -4.2528
75112 | KBRU132 132.00 | KBRU | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 15.169 | 2.7958
75112 | KBRU132 132.00 | KBRU | T3 | 12 | KELANTAN | 1 | TNB T | 1 | 24.9265 | 10.2017
75112 | KBRU132 132.00 | KBRU | T4 | 12 | KELANTAN | 1 | TNB T | 1 | 8.5346 | 1.4248
75112 | KBRU132 132.00 | KBRU | T5 | 12 | KELANTAN | 1 | TNB T | 1 | 24.9814 | 10.2131
75131 | KDIS132 132.00 | KDIS | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 17.123 | 1.1815
75131 | KDIS132 132.00 | KDIS | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 17.0764 | 1.1763
75113 | KKRI132 132.00 | KKRI | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 8.8556 | 1.0738
75113 | KKRI132 132.00 | KKRI | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 8.7935 | 1.0541
75132 | LMAL132 132.00 | LMAL | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 38.8219 | 7.7797
75132 | LMAL132 132.00 | LMAL | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 38.4885 | 7.7859
75947 | MALS_LSS2 33.000 | MALS | X1 | 12 | KELANTAN | 1 | TNB T | 1 | 0 | 0
75129 | PCOR132 132.00 | PCOR | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 38.9658 | 5.8609
75129 | PCOR132 132.00 | PCOR | T3 | 12 | KELANTAN | 1 | TNB T | 1 | 32.9402 | 16.9729
75129 | PCOR132 132.00 | PCOR | T4 | 12 | KELANTAN | 1 | TNB T | 1 | 29.6256 | -4.7975
75208 | PGAU275 275.00 | PGAU | N1 | 12 | KELANTAN | 1 | TNB T | 1 | 0 | 0
75208 | PGAU275 275.00 | PGAU | N2 | 12 | KELANTAN | 1 | TNB T | 1 | 0 | 0
75114 | PPTH132 132.00 | PPTH | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 19.6103 | 2.9791
75114 | PPTH132 132.00 | PPTH | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 19.1226 | 2.1652
75134 | RPJG132 132.00 | RPJG | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 6.3259 | -1.1919
75134 | RPJG132 132.00 | RPJG | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 6.1819 | -0.7
75106 | SJTH132 132.00 | SJTH | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 21.3261 | -2.2284
75106 | SJTH132 132.00 | SJTH | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 21.5291 | -2.2253
75106 | SJTH132 132.00 | SJTH | T5 | 12 | KELANTAN | 1 | TNB T | 1 | 14.8915 | -0.2537
75127 | TJUG132 132.00 | TJUG | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 26.6216 | 2.0969
75127 | TJUG132 132.00 | TJUG | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 30.4043 | 4.5883
75101 | TMRH132 132.00 | TMRH | T1 | 12 | KELANTAN | 1 | TNB T | 1 | 0 | 0
75101 | TMRH132 132.00 | TMRH | T2 | 12 | KELANTAN | 1 | TNB T | 1 | 33.809 | 4.9207
75101 | TMRH132 132.00 | TMRH | T3 | 12 | KELANTAN | 1 | TNB T | 1 | 34.0472 | 5.0004
61103 | TEWA132 132.00 | TEWA | T1 | 15 | LANGKAWI | 1 | TNB T | 1 | 0 | 0
61103 | TEWA132 132.00 | TEWA | T2 | 15 | LANGKAWI | 1 | TNB T | 1 | 33.2882 | -6.3952
61125 | UMKA132 132.00 | UMKA | T1 | 15 | LANGKAWI | 1 | TNB T | 1 | 3.7268 | 0.4535
61125 | UMKA132 132.00 | UMKA | T2 | 15 | LANGKAWI | 1 | TNB T | 1 | 3.7237 | 0.5064
61125 | UMKA132 132.00 | UMKA | T3 | 15 | LANGKAWI | 1 | TNB T | 1 | 17.299 | 0.4587
61125 | UMKA132 132.00 | UMKA | T4 | 15 | LANGKAWI | 1 | TNB T | 1 | 17.1541 | 0.4774
61114 | CIMA132 132.00 | CIMA | F1 | 1 | PERLIS | 100 | LPC | 1 | 1.0251 | 0.7248
61114 | CIMA132 132.00 | CIMA | F2 | 1 | PERLIS | 100 | LPC | 1 | 16.0399 | 7.2692
61130 | KBRI132 132.00 | KBRI | F1 | 1 | PERLIS | 100 | LPC | 1 | 0.4712 | 0.1118
61130 | KBRI132 132.00 | KBRI | F2 | 1 | PERLIS | 100 | LPC | 1 | 0.4608 | 0.1325
61118 | KHTC132 132.00 | KHTC | F1 | 2 | KEDAH | 100 | LPC | 1 | 11.7198 | -0.7746
61118 | KHTC132 132.00 | KHTC | F3 | 2 | KEDAH | 100 | LPC | 1 | 11.8699 | 0.6265
61118 | KHTC132 132.00 | KHTC | F4 | 2 | KEDAH | 100 | LPC | 1 | 0 | 0
1962 | KHTE132 132.00 | KHTE | F1 | 2 | KEDAH | 100 | LPC | 1 | 0 | 0
1962 | KHTE132 132.00 | KHTE | F2 | 2 | KEDAH | 100 | LPC | 1 | 0 | 0
1962 | KHTE132 132.00 | KHTE | F3 | 2 | KEDAH | 100 | LPC | 1 | 0 | 0
1962 | KHTE132 132.00 | KHTE | F4 | 2 | KEDAH | 100 | LPC | 1 | 0 | 0
61129 | KTJG132 132.00 | KTJG | F1 | 2 | KEDAH | 100 | LPC | 1 | 0.3645 | 0.0559
61129 | KTJG132 132.00 | KTJG | F2 | 2 | KEDAH | 100 | LPC | 1 | 0.5229 | -0.0601
61134 | PFTZ132 132.00 | PFTZ | F1 | 2 | KEDAH | 100 | LPC | 1 | 8.2084 | 4.287
61134 | PFTZ132 132.00 | PFTZ | F2 | 2 | KEDAH | 100 | LPC | 1 | 6.8136 | 3.2318
61225 | PWGR275 275.00 | PWGR | F1 | 2 | KEDAH | 100 | LPC | 1 | 0 | 0
61225 | PWGR275 275.00 | PWGR | F2 | 2 | KEDAH | 100 | LPC | 1 | 0 | 0
62148 | IBDN132 132.00 | IBDN | F1 | 3 | P PINANG | 100 | LPC | 1 | 0 | 0
62148 | IBDN132 132.00 | IBDN | F2 | 3 | P PINANG | 100 | LPC | 1 | 9.8466 | 3.2214
62143 | INTL132 132.00 | INTL | F1 | 3 | P PINANG | 100 | LPC | 1 | 0.0269 | -0.0611
562143 | INTL132R 132.00 | INTL | F2 | 3 | P PINANG | 100 | LPC | 1 | 22.4672 | 5.5202
62126 | JNKO132 132.00 | JNKO | F1 | 3 | P PINANG | 100 | LPC | 1 | 0.3334 | -0.407
62126 | JNKO132 132.00 | JNKO | F2 | 3 | P PINANG | 100 | LPC | 1 | 0.0332 | 0.1543
61128 | KGRN132 132.00 | KGRN | F1 | 3 | P PINANG | 100 | LPC | 1 | 0.845 | -0.0621
61118 | KHTC132 132.00 | KHTC | F2 | 3 | P PINANG | 100 | LPC | 1 | 12.631 | -0.1481
62121 | KSMP132 132.00 | KSMP | F1 | 3 | P PINANG | 100 | LPC | 1 | 0.8388 | 0.1916
62121 | KSMP132 132.00 | KSMP | F2 | 3 | P PINANG | 100 | LPC | 1 | 0.2268 | -0.0818
62123 | KTGR132 132.00 | KTGR | F1 | 3 | P PINANG | 100 | LPC | 1 | 0.6441 | -0.1077
62123 | KTGR132 132.00 | KTGR | F2 | 3 | P PINANG | 100 | LPC | 1 | 0 | 0
62145 | MCRN132 132.00 | MCRN | F1 | 3 | P PINANG | 100 | LPC | 1 | 14.557 | -0.5405
62145 | MCRN132 132.00 | MCRN | F2 | 3 | P PINANG | 100 | LPC | 1 | 15.2156 | -0.4784
62146 | MWTA132 132.00 | MWTA | F1 | 3 | P PINANG | 100 | LPC | 1 | 18.3635 | -28.6232
562146 | MWTA132R 132.00 | MWTA | F2 | 3 | P PINANG | 100 | LPC | 1 | 35.8862 | 16.5514
62147 | SAND132 132.00 | SAND | F1 | 3 | P PINANG | 100 | LPC | 1 | 10.0578 | 3.0827
62147 | SAND132 132.00 | SAND | F2 | 3 | P PINANG | 100 | LPC | 1 | 8.3772 | 2.6281
662144 | SRNW132 132.00 | SRNW | F1 | 3 | P PINANG | 100 | LPC | 1 | 11.6307 | 3.3623
62144 | SRON132 132.00 | SRON | F1 | 3 | P PINANG | 100 | LPC | 1 | 0 | 0
62144 | SRON132 132.00 | SRON | F2 | 3 | P PINANG | 100 | LPC | 1 | 15.2467 | 5.4126
62144 | SRON132 132.00 | SRON | F3 | 3 | P PINANG | 100 | LPC | 1 | 0 | 0
562144 | SRON132R 132.00 | SRON | F3 | 3 | P PINANG | 100 | LPC | 1 | 0 | 0
63137 | APMC132 132.00 | APMC | F1 | 4 | PERAK | 100 | LPC | 1 | 12.0573 | 3.8769
563137 | APMC132R 132.00 | APMC | F2 | 4 | PERAK | 100 | LPC | 1 | 10.5072 | 4.3843
63114 | HUME132 132.00 | HUME | F1 | 4 | PERAK | 100 | LPC | 1 | 6.7597 | 3.2111
563114 | HUME132R 132.00 | HUME | F2 | 4 | PERAK | 100 | LPC | 1 | 16.8403 | 4.4734
63110 | KBMH132 132.00 | KBMH | F1 | 4 | PERAK | 100 | LPC | 1 | 0.0238 | -0.1253
63110 | KBMH132 132.00 | KBMH | F2 | 4 | PERAK | 100 | LPC | 1 | 0.1336 | -0.0694
63199 | KLHT132 132.00 | KLHT | F1 | 4 | PERAK | 100 | LPC | 1 | 0.9879 | 0.3241
63199 | KLHT132 132.00 | KLHT | F2 | 4 | PERAK | 100 | LPC | 1 | 0.8232 | 0.2288
63197 | KSKI132 132.00 | KSKI | F1 | 4 | PERAK | 100 | LPC | 1 | 1.372 | 0.2682
63108 | KSPT132 132.00 | KSPT | F1 | 4 | PERAK | 100 | LPC | 1 | 0.5633 | 0.1274
563108 | KSPT132R 132.00 | KSPT | F2 | 4 | PERAK | 100 | LPC | 1 | 0.8626 | 0.1967
63109 | KTPG132 132.00 | KTPG | F1 | 4 | PERAK | 100 | LPC | 1 | 0.1864 | -0.1243
63109 | KTPG132 132.00 | KTPG | F2 | 4 | PERAK | 100 | LPC | 1 | 0.2071 | -0.0725
63122 | PHCT132 132.00 | PHCT | F1 | 4 | PERAK | 100 | LPC | 1 | 8.3057 | 4.6069
63122 | PHCT132 132.00 | PHCT | F2 | 4 | PERAK | 100 | LPC | 1 | 8.373 | 5.1661
63103 | TCOP132 132.00 | TCOP | F1 | 4 | PERAK | 100 | LPC | 1 | 10.0754 | 1.1525
63103 | TCOP132 132.00 | TCOP | F2 | 4 | PERAK | 100 | LPC | 1 | 6.3373 | 2.0172
63217 | VALE275 275.00 | VALE | F1 | 4 | PERAK | 100 | LPC | 1 | 4.5458 | 3.1376
63217 | VALE275 275.00 | VALE | F2 | 4 | PERAK | 100 | LPC | 1 | 4.2766 | 3.21
51000 | APMR132 132.00 | APMR | F2 | 5 | SELANGOR | 100 | LPC | 1 | 0.0249 | 0.0197
551000 | APMR132R 132.00 | APMR | F1 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51999 | ASMB132 132.00 | ASMB | F1 | 5 | SELANGOR | 100 | LPC | 1 | 3.2608 | 1.8287
51999 | ASMB132 132.00 | ASMB | F2 | 5 | SELANGOR | 100 | LPC | 1 | 3.2504 | 1.839
52004 | ELPN275 275.00 | ELPN | F1 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
52004 | ELPN275 275.00 | ELPN | F2 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51210 | ERLA132 132.00 | ERLA | F1 | 5 | SELANGOR | 100 | LPC | 1 | 3.9867 | -1.139
51210 | ERLA132 132.00 | ERLA | F2 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51076 | ESMI132 132.00 | ESMI | T1 | 5 | SELANGOR | 100 | LPC | 1 | 0.0499 | -0.0787
51076 | ESMI132 132.00 | ESMI | T2 | 5 | SELANGOR | 100 | LPC | 1 | 0.0499 | -0.0787
51115 | KJKM132 132.00 | KJKM | F1 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51126 | KKPG132 132.00 | KKPG | F1 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51126 | KKPG132 132.00 | KKPG | F2 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51118 | KRWG132 132.00 | KRWG | F1 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51118 | KRWG132 132.00 | KRWG | F2 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51211 | KSAS132 132.00 | KSAS | F1 | 5 | SELANGOR | 100 | LPC | 1 | 0.2744 | 0.0414
51120 | KSJS132 132.00 | KSJS | F1 | 5 | SELANGOR | 100 | LPC | 1 | 0.5074 | 0.1822
51086 | LCCT132 132.00 | LCCT | T1 | 5 | SELANGOR | 100 | LPC | 1 | 12.3566 | -7.5156
51086 | LCCT132 132.00 | LCCT | T2 | 5 | SELANGOR | 100 | LPC | 1 | 12.4653 | -7.6347
52038 | MGST275 275.00 | MGST | F1 | 5 | SELANGOR | 100 | LPC | 1 | 2.3816 | -1.8639
52038 | MGST275 275.00 | MGST | F2 | 5 | SELANGOR | 100 | LPC | 1 | 1.0355 | 1.4497
50114 | MOXY132 132.00 | MOXY | F1 | 5 | SELANGOR | 100 | LPC | 1 | 8.7582 | 3.0444
50114 | MOXY132 132.00 | MOXY | F2 | 5 | SELANGOR | 100 | LPC | 1 | 7.0466 | 3.3809
51012 | MSWK132 132.00 | MSWK | F1 | 5 | SELANGOR | 100 | LPC | 1 | 57.5012 | 22.3875
51064 | NEGM132 132.00 | NEGM | F1 | 5 | SELANGOR | 100 | LPC | 1 | 25.8264 | 10.7951
51064 | NEGM132 132.00 | NEGM | F2 | 5 | SELANGOR | 100 | LPC | 1 | 26.5813 | 10.1199
51064 | NEGM132 132.00 | NEGM | T3 | 5 | SELANGOR | 100 | LPC | 1 | 16.5997 | 10.2207
551064 | NEGM132N 132.00 | NEGM | F3 | 5 | SELANGOR | 100 | LPC | 1 | 0 | 0
51044 | SGLC132 132.00 | SGLC | F1 | 5 | SELANGOR | 100 | LPC | 1 | 0.2837 | 0.2537
51044 | SGLC132 132.00 | SGLC | F2 | 5 | SELANGOR | 100 | LPC | 1 | 0.2237 | 0.2237
51128 | BCDC132 132.00 | BCDC | T1 | 6 | WPKL | 100 | LPC | 1 | 1.2571 | 5.7498
51080 | BUTM132 132.00 | BUTM | F1 | 6 | WPKL | 100 | LPC | 1 | 17.0857 | -5.0739
51080 | BUTM132 132.00 | BUTM | F2 | 6 | WPKL | 100 | LPC | 1 | 13.7721 | 7.4556
51070 | FSCL132 132.00 | FSCL | F1 | 6 | WPKL | 100 | LPC | 1 | 0 | 0
551070 | FSCL132R 132.00 | FSCL | F2 | 6 | WPKL | 100 | LPC | 1 | 24.2949 | 11.6204
51077 | HNQC132 132.00 | HNQC | F1 | 6 | WPKL | 100 | LPC | 1 | 10.8355 | 3.7174
51077 | HNQC132 132.00 | HNQC | F2 | 6 | WPKL | 100 | LPC | 1 | 10.6366 | 3.8075
88110 | KLCP132 132.00 | KLCP | F1 | 6 | WPKL | 100 | LPC | 1 | 1.0635 | 6.2534
88110 | KLCP132 132.00 | KLCP | F2 | 6 | WPKL | 100 | LPC | 1 | 10.1199 | -1.8991
51116 | KSLS132 132.00 | KSLS | F1 | 6 | WPKL | 100 | LPC | 1 | 1.926 | 0.817
51116 | KSLS132 132.00 | KSLS | F2 | 6 | WPKL | 100 | LPC | 1 | 0.5996 | 0.1429
88147 | KTST132 132.00 | KTST | F1 | 6 | WPKL | 100 | LPC | 1 | 0 | 0
88196 | LJTK132 132.00 | LJTK | F1 | 6 | WPKL | 100 | LPC | 1 | 3.5683 | -0.3728
88196 | LJTK132 132.00 | LJTK | F2 | 6 | WPKL | 100 | LPC | 1 | 3.6087 | -0.3728
88198 | LKRC132 132.00 | LKRC | F1 | 6 | WPKL | 100 | LPC | 1 | 4.4734 | -0.9112
88198 | LKRC132 132.00 | LKRC | F2 | 6 | WPKL | 100 | LPC | 1 | 4.4837 | -0.9112
51033 | MBSD132 132.00 | MBSD | F1 | 6 | WPKL | 100 | LPC | 1 | 2.6343 | -1.5657
51033 | MBSD132 132.00 | MBSD | F2 | 6 | WPKL | 100 | LPC | 1 | 2.5152 | -1.6744
88151 | MJJG132 132.00 | MJJG | F1 | 6 | WPKL | 100 | LPC | 1 | 2.7658 | -1.2229
88151 | MJJG132 132.00 | MJJG | F2 | 6 | WPKL | 100 | LPC | 1 | 3.4316 | -1.1473
88126 | MKCL132 132.00 | MKCL | F1 | 6 | WPKL | 100 | LPC | 1 | 3.3208 | -1.0925
88126 | MKCL132 132.00 | MKCL | F2 | 6 | WPKL | 100 | LPC | 1 | 3.1562 | -1.195
74148 | UKLI132 132.00 | UKLI | F1 | 6 | WPKL | 100 | LPC | 1 | 21.1035 | 3.0444
74148 | UKLI132 132.00 | UKLI | F2 | 6 | WPKL | 100 | LPC | 1 | 21.7351 | 3.1065
96194 | HLNN132 132.00 | HLNN | F1 | 7 | NS | 100 | LPC | 1 | 0.1118 | -0.0746
96194 | HLNN132 132.00 | HLNN | F2 | 7 | NS | 100 | LPC | 1 | 10.7143 | 5.0843
96194 | HLNN132 132.00 | HLNN | F3 | 7 | NS | 100 | LPC | 1 | 10.8686 | 3.704
96194 | HLNN132 132.00 | HLNN | F4 | 7 | NS | 100 | LPC | 1 | 0 | 0
96148 | KBBR132 132.00 | KBBR | F1 | 7 | NS | 100 | LPC | 1 | 0.9775 | 0.2537
96148 | KBBR132 132.00 | KBBR | F2 | 7 | NS | 100 | LPC | 1 | 0.904 | 0.3572
96151 | NSCI132 132.00 | NSCI | T1 | 7 | NS | 100 | LPC | 1 | 12.6745 | 5.3877
96151 | NSCI132 132.00 | NSCI | T2 | 7 | NS | 100 | LPC | 1 | 13.5692 | 5.4581
96141 | SHEL132 132.00 | SHEL | F1 | 7 | NS | 100 | LPC | 1 | 15.9394 | 4.1824
96141 | SHEL132 132.00 | SHEL | F2 | 7 | NS | 100 | LPC | 1 | 16.3868 | 8.8649
96193 | SSUN132 132.00 | SSUN | T3 | 7 | NS | 100 | LPC | 1 | 0 | 0
96193 | SSUN132 132.00 | SSUN | T4 | 7 | NS | 100 | LPC | 1 | 0 | 0
96193 | SSUN132 132.00 | SSUN | T5 | 7 | NS | 100 | LPC | 1 | 0 | 0
596193 | SSUN132N 132.00 | SSUN | T1 | 7 | NS | 100 | LPC | 1 | 18.5282 | 6.768
596193 | SSUN132N 132.00 | SSUN | T2 | 7 | NS | 100 | LPC | 1 | 19.2717 | 7.1729
96196 | HLNM132 132.00 | HLNM | F1 | 8 | MELAKA | 100 | LPC | 1 | 9.539 | 4.1938
96199 | ONST132 132.00 | ONST | F1 | 8 | MELAKA | 100 | LPC | 1 | 9.5577 | -1.429
96197 | PPSR132 132.00 | PPSR | F1 | 8 | MELAKA | 100 | LPC | 1 | 2.7441 | -3.6035
96197 | PPSR132 132.00 | PPSR | F2 | 8 | MELAKA | 100 | LPC | 1 | 0.1243 | -1.5709
96181 | SPWR132 132.00 | SPWR | F1 | 8 | MELAKA | 100 | LPC | 1 | 0.146 | 0.0445
96181 | SPWR132 132.00 | SPWR | F2 | 8 | MELAKA | 100 | LPC | 1 | 0.1864 | 0.1719
96181 | SPWR132 132.00 | SPWR | F3 | 8 | MELAKA | 100 | LPC | 1 | 0.1046 | 0.3593
96127 | TIEM132 132.00 | TIEM | T1 | 8 | MELAKA | 100 | LPC | 1 | 7.1226 | 2.9034
96127 | TIEM132 132.00 | TIEM | T2 | 8 | MELAKA | 100 | LPC | 1 | 6.8323 | 2.2433
96124 | XNYI132 132.00 | XNYI | F1 | 8 | MELAKA | 100 | LPC | 1 | 9.9734 | -0.0566
96124 | XNYI132 132.00 | XNYI | F2 | 8 | MELAKA | 100 | LPC | 1 | 27.8171 | 8.038
97160 | ASTM132 132.00 | ASTM | F1 | 9 | JOHOR | 100 | LPC | 1 | 0.1646 | 0.0445
97160 | ASTM132 132.00 | ASTM | F2 | 9 | JOHOR | 100 | LPC | 1 | 0 | 0
97405 | ATDC132 132.00 | ATDC | T1 | 9 | JOHOR | 100 | LPC | 1 | 8.1918 | -0.0797
97405 | ATDC132 132.00 | ATDC | T2 | 9 | JOHOR | 100 | LPC | 1 | 7.4162 | -0.2185
97405 | ATDC132 132.00 | ATDC | T3 | 9 | JOHOR | 100 | LPC | 1 | 1.2474 | 0.9249
97246 | BRDC275 275.00 | BRDC | T1 | 9 | JOHOR | 100 | LPC | 1 | 93.3606 | 4.2041
97246 | BRDC275 275.00 | BRDC | T2 | 9 | JOHOR | 100 | LPC | 1 | 90.5699 | 5.6538
97211 | BSTL275 275.00 | BSTL | F1 | 9 | JOHOR | 100 | LPC | 1 | 4.4526 | -3.0029
97211 | BSTL275 275.00 | BSTL | F2 | 9 | JOHOR | 100 | LPC | 1 | 0 | 0
97403 | GDSD132 132.00 | GDSD | T1 | 9 | JOHOR | 100 | LPC | 1 | 48.713 | 3.6636
97403 | GDSD132 132.00 | GDSD | T2 | 9 | JOHOR | 100 | LPC | 1 | 4.2487 | 0.3759
97403 | GDSD132 132.00 | GDSD | T3 | 9 | JOHOR | 100 | LPC | 1 | 42.6677 | 3.705
97403 | GDSD132 132.00 | GDSD | T4 | 9 | JOHOR | 100 | LPC | 1 | 4.2497 | 0.2765
97402 | KISW132 132.00 | KISW | F1 | 9 | JOHOR | 100 | LPC | 1 | 6.5236 | 2.7958
97402 | KISW132 132.00 | KISW | F2 | 9 | JOHOR | 100 | LPC | 1 | 7.5902 | 2.8373
97161 | KRGM132 132.00 | KRGM | F1 | 9 | JOHOR | 100 | LPC | 1 | 2.7586 | 0.6265
97161 | KRGM132 132.00 | KRGM | F2 | 9 | JOHOR | 100 | LPC | 1 | 2.7586 | 0.6265
96175 | KRMB132 132.00 | KRMB | F1 | 9 | JOHOR | 100 | LPC | 1 | 0.7497 | -0.6213
96175 | KRMB132 132.00 | KRMB | F2 | 9 | JOHOR | 100 | LPC | 1 | 1.2219 | 0.2858
97401 | MMHE132 132.00 | MMHE | F1 | 9 | JOHOR | 100 | LPC | 1 | 1.5574 | 0.7828
97401 | MMHE132 132.00 | MMHE | F2 | 9 | JOHOR | 100 | LPC | 1 | 6.1923 | 1.0324
97409 | PTDC132 132.00 | PTDC | T1 | 9 | JOHOR | 100 | LPC | 1 | 19.4218 | 1.1556
97409 | PTDC132 132.00 | PTDC | T2 | 9 | JOHOR | 100 | LPC | 1 | 19.4467 | 1.1432
97199 | PTPS132 132.00 | PTPS | F1 | 9 | JOHOR | 100 | LPC | 1 | 9.6829 | 3.0226
97199 | PTPS132 132.00 | PTPS | F2 | 9 | JOHOR | 100 | LPC | 1 | 10.1199 | 1.7893
97196 | STME132 132.00 | STME | F1 | 9 | JOHOR | 100 | LPC | 1 | 14.0766 | 5.5586
97196 | STME132 132.00 | STME | F2 | 9 | JOHOR | 100 | LPC | 1 | 13.2471 | 5.3991
97183 | TLTP132 132.00 | TLTP | F1 | 9 | JOHOR | 100 | LPC | 1 | 24.1996 | 7.8346
97171 | TTAN132 132.00 | TTAN | F1 | 9 | JOHOR | 100 | LPC | 1 | 13.5019 | 5.8154
97171 | TTAN132 132.00 | TTAN | F2 | 9 | JOHOR | 100 | LPC | 1 | 12.7346 | 5.9645
97159 | UTMJ132 132.00 | UTMJ | F1 | 9 | JOHOR | 100 | LPC | 1 | 4.0799 | -0.9837
597159 | UTMJ132R 132.00 | UTMJ | F2 | 9 | JOHOR | 100 | LPC | 1 | 1.3565 | -0.4556
97247 | YWDC275 275.00 | YWDC | T1 | 9 | JOHOR | 100 | LPC | 1 | 5.6383 | -0.6834
97247 | YWDC275 275.00 | YWDC | T2 | 9 | JOHOR | 100 | LPC | 1 | 0.6265 | -1.253
74130 | AMCO132 132.00 | AMCO | F1 | 10 | PAHANG | 100 | LPC | 1 | 3.5621 | 2.5473
74130 | AMCO132 132.00 | AMCO | F2 | 10 | PAHANG | 100 | LPC | 1 | 4.2145 | 3.2722
74130 | AMCO132 132.00 | AMCO | F3 | 10 | PAHANG | 100 | LPC | 1 | 0 | 0
75207 | ASSB275 275.00 | ASSB | F1 | 10 | PAHANG | 100 | LPC | 1 | 23.6094 | -1.7603
74124 | GHLD132 132.00 | GHLD | F3 | 10 | PAHANG | 100 | LPC | 1 | 0 | 0
74124 | GHLD132 132.00 | GHLD | F4 | 10 | PAHANG | 100 | LPC | 1 | 0 | 0
74124 | GHLD132 132.00 | GHLD | T1 | 10 | PAHANG | 100 | LPC | 1 | 7.148 | 2.0254
74124 | GHLD132 132.00 | GHLD | T2 | 10 | PAHANG | 100 | LPC | 1 | 7.148 | 2.0254
74146 | JDSI132 132.00 | JDSI | F1 | 10 | PAHANG | 100 | LPC | 1 | 0.1139 | -2.2677
74146 | JDSI132 132.00 | JDSI | F2 | 10 | PAHANG | 100 | LPC | 1 | 0 | 0
74140 | KNKA132 132.00 | KNKA | F1 | 10 | PAHANG | 100 | LPC | 1 | 0 | 0
74140 | KNKA132 132.00 | KNKA | F2 | 10 | PAHANG | 100 | LPC | 1 | 0 | 0
74154 | KSTL132 132.00 | KSTL | F1 | 10 | PAHANG | 100 | LPC | 1 | 0 | 0
74147 | MNID132 132.00 | MNID | F1 | 10 | PAHANG | 100 | LPC | 1 | 0.321 | -0.1035
74134 | MTBE132 132.00 | MTBE | F1 | 10 | PAHANG | 100 | LPC | 1 | 4.8254 | 1.9467
74134 | MTBE132 132.00 | MTBE | F2 | 10 | PAHANG | 100 | LPC | 1 | 3.966 | 1.5429
74131 | PCMT132 132.00 | PCMT | F1 | 10 | PAHANG | 100 | LPC | 1 | 6.5651 | 3.5207
74131 | PCMT132 132.00 | PCMT | F2 | 10 | PAHANG | 100 | LPC | 1 | 3.4896 | 0.0518
74131 | PCMT132 132.00 | PCMT | F3 | 10 | PAHANG | 100 | LPC | 1 | 0 | 0
74131 | PCMT132 132.00 | PCMT | F4 | 10 | PAHANG | 100 | LPC | 1 | 12.1982 | 4.5562
75207 | ASSB275 275.00 | ASSB | F2 | 11 | TGANU | 100 | LPC | 1 | 22.1597 | 2.1745
75128 | CJDG132 132.00 | CJDG | F1 | 11 | TGANU | 100 | LPC | 1 | 17.6656 | 9.8476
75128 | CJDG132 132.00 | CJDG | F2 | 11 | TGANU | 100 | LPC | 1 | 15.0354 | 5.3742
75119 | EMSB132 132.00 | EMSB | F1 | 11 | TGANU | 100 | LPC | 1 | 8.0562 | 4.1834
75119 | EMSB132 132.00 | EMSB | F2 | 11 | TGANU | 100 | LPC | 1 | 16.2884 | 3.3343
75212 | ESTL275 275.00 | ESTL | F1 | 11 | TGANU | 100 | LPC | 1 | 5.7677 | 4.6287
75212 | ESTL275 275.00 | ESTL | F2 | 11 | TGANU | 100 | LPC | 1 | 5.747 | 4.7012
75122 | HTXD132 132.00 | HTXD | F1 | 11 | TGANU | 100 | LPC | 1 | 3.2722 | 1.3358
75122 | HTXD132 132.00 | HTXD | F2 | 11 | TGANU | 100 | LPC | 1 | 3.2308 | 1.3358
75147 | KGPP132 132.00 | KGPP | F1 | 11 | TGANU | 100 | LPC | 1 | 3.179 | 0.1243
75147 | KGPP132 132.00 | KGPP | F2 | 11 | TGANU | 100 | LPC | 1 | 3.4068 | 0.176
75139 | PGPP132 132.00 | PGPP | F1 | 11 | TGANU | 100 | LPC | 1 | 4.7043 | -0.1646
75139 | PGPP132 132.00 | PGPP | F2 | 11 | TGANU | 100 | LPC | 1 | 4.7043 | -0.1709
75210 | PWSM275 275.00 | PWSM | F1 | 11 | TGANU | 100 | LPC | 1 | 0 | 0
75210 | PWSM275 275.00 | PWSM | F2 | 11 | TGANU | 100 | LPC | 1 | 0 | 0
61145 | KCMT132 132.00 | KCMT | F1 | 15 | LANGKAWI | 100 | LPC | 1 | 0 | 0
561145 | KCMT132R 132.00 | KCMT | F2 | 15 | LANGKAWI | 100 | LPC | 1 | 26.1764 | 10.0278

## UFLS 2024
UFLS2024
Bus Number | Id | Hz | Substation | Zone | Load (PSSE)
97178 | T2 | 49.2 | CBRU132 | JOHOR | 8.9519
97178 | T1 | 49.2 | CBRU132 | JOHOR | 8.9871
97153 | T2 | 49.2 | PGDT132 | JOHOR | 10.1427
97153 | T1 | 49.2 | PGDT132 | JOHOR | 2.4873
97192 | T2 | 49.2 | TMPI132 | JOHOR | 27.9139
97192 | T1 | 49.2 | TMPI132 | JOHOR | 29.0913
62128 | T2 | 49.2 | SARA132 | P PINANG | 35.7174
62128 | T1 | 49.2 | SARA132 | P PINANG | 35.6077
74115 | T2 | 49.2 | PKNI132 | PAHANG | 6.3124
74115 | T1 | 49.2 | PKNI132 | PAHANG | 6.2824
96106 | T2 | 49.2 | HPGH132 | MELAKA | 6.0111
96106 | T1 | 49.2 | HPGH132 | MELAKA | 5.9893
96169 | T2 | 49.2 | ESTK132 | SELANGOR | 22.8441
96169 | T1 | 49.2 | ESTK132 | SELANGOR | 22.637
63145 | T2 | 49.2 | PKID132 | PERAK | 9.6612
63145 | T1 | 49.2 | PKID132 | PERAK | 5.4146
63145 | T4 | 49.2 | PKID132 | PERAK | 12.6579
63145 | T3 | 49.2 | PKID132 | PERAK | 12.6652
63173 | T4 | 49.2 | KVRT132 | PERAK | 33.9333
63173 | T3 | 49.2 | KVRT132 | PERAK | 33.9395
63146 | T4 | 49.2 | MLBU132 | PERAK | 34.6333
63146 | T3 | 49.2 | MLBU132 | PERAK | 34.4842
51013 | T2 | 49.2 | STIA132 | SELANGOR | 36.9797
51013 | T1 | 49.2 | STIA132 | SELANGOR | 33.1173
88104 | T2 | 49.2 | DCTY132 | WPKL | 12.9489
88104 | T1 | 49.2 | DCTY132 | WPKL | 12.8951
88128 | T2 | 49.2 | MJLR132 | WPKL | 49.3467
88128 | T1 | 49.2 | MJLR132 | WPKL | 49.94
88142 | T2 | 49.2 | SHMS132 | WPKL | 28.1138
88142 | T1 | 49.2 | SHMS132 | WPKL | 28.2235
88107 | T2 | 49.2 | SCTY132 | WPKL | 17.0774
88107 | T1 | 49.2 | SCTY132 | WPKL | 17.1303
51038 | T3 | 49.2 | CJYA132 | SELANGOR | 66.9274
51038 | T2 | 49.2 | CJYA132 | SELANGOR | 33.5056
51038 | T1 | 49.2 | CJYA132 | SELANGOR | 31.8343
88195 | T4 | 49.2 | DDSA132 | WPKL | 30.6943
88195 | T3 | 49.2 | DDSA132 | WPKL | 30.6777
61119 | T2 | 49.2 | MGON132 | KEDAH | 8.2529
61119 | T1 | 49.2 | MGON132 | KEDAH | 8.2591
61132 | T2 | 49.2 | PAUH132 | KEDAH | 18.9869
61132 | T1 | 49.2 | PAUH132 | KEDAH | 18.8088
63127 | T4 | 49.1 | TMOH132 | PERAK | 11.2144
63127 | T3 | 49.1 | TMOH132 | PERAK | 11.3905
63155 | T4 | 49.1 | KLBG132 | PERAK | 11.2352
63155 | T3 | 49.1 | KLBG132 | PERAK | 11.2807
63142 | T2 | 49.1 | NKAN132 | PERAK | 14.8076
63142 | T1 | 49.1 | NKAN132 | PERAK | 14.7455
63134 | T2 | 49.1 | TASK132 | PERAK | 4.7219
63134 | T1 | 49.1 | TASK132 | PERAK | 4.8461
88162 | T5 | 49.1 | SPKC132 | WPKL | 55.7688
88162 | T4 | 49.1 | SPKC132 | WPKL | 49.4036
88162 | T3 | 49.1 | SPKC132 | WPKL | 49.6522
51023 | T2 | 49.1 | NUNI132 | SELANGOR | 13.096
51023 | T1 | 49.1 | NUNI132 | SELANGOR | 12.719
97186 | T2 | 49.1 | TBRU132 | JOHOR | 0
97186 | T1 | 49.1 | TBRU132 | JOHOR | 23.2293
74145 | T2 | 49.1 | KRYG132 | PAHANG | 0
74145 | T1 | 49.1 | KRYG132 | PAHANG | 31.6769
96141 | F2 | 49.1 | SHEL132 | NS | 19.1541
96141 | F1 | 49.1 | SHEL132 | NS | 18.1541
51072 | T2 | 49.1 | HCOM132 | SELANGOR | 34.0078
51072 | T1 | 49.1 | HCOM132 | SELANGOR | 38.7888
51017 | T5 | 49.1 | SHAE132 | SELANGOR | 32.8543
51017 | T4 | 49.1 | SHAE132 | SELANGOR | 24.0681
51017 | T3 | 49.1 | SHAE132 | SELANGOR | 23.7854
51007 | T2 | 49.1 | SHAS132 | SELANGOR | 39.0476
51007 | T1 | 49.1 | SHAS132 | SELANGOR | 38.9275
75129 | T4 | 49.1 | PCOR132 | KELANTAN | 29.6256
75129 | T3 | 49.1 | PCOR132 | KELANTAN | 32.9402
75129 | T2 | 49.1 | PCOR132 | KELANTAN | 38.9658
97110 | T2 | 49.1 | JTGH132 | JOHOR | 12.2458
97110 | T1 | 49.1 | JTGH132 | JOHOR | 12.193
62112 | T2 | 49.1 | SJAY132 | P PINANG | 42.9918
62112 | T1 | 49.1 | SJAY132 | P PINANG | 42.5776
61127 | T4 | 49.1 | INTN132 | KEDAH | 24.5185
61127 | T3 | 49.1 | INTN132 | KEDAH | 25.3708
61127 | T2 | 49.1 | INTN132 | KEDAH | 15.0354
61127 | T1 | 49.1 | INTN132 | KEDAH | 16.5214
96177 | T2 | 49.1 | MPSS132 | MELAKA | 6.0121
96177 | T1 | 49.1 | MPSS132 | MELAKA | 2.9429
75127 | T2 | 49 | TJUG132 | KELANTAN | 30.4043
75127 | T1 | 49 | TJUG132 | KELANTAN | 26.6216
97147 | T3 | 49 | MUAR132 | JOHOR | 12.6041
97147 | T2 | 49 | MUAR132 | JOHOR | 9.4168
51004 | T2 | 49 | BRGS132 | SELANGOR | 10.8178
51004 | T1 | 49 | BRGS132 | SELANGOR | 8.0603
51047 | T2 | 49 | IGBK132 | SELANGOR | 11.6069
51047 | T1 | 49 | IGBK132 | SELANGOR | 10.7733
51087 | T4 | 49 | BBTG132 | SELANGOR | 19.8681
51087 | T3 | 49 | BBTG132 | SELANGOR | 20.0307
74128 | T4 | 49 | BIMK132 | PAHANG | 37.6424
74128 | T3 | 49 | BIMK132 | PAHANG | 37.4146
74128 | T2 | 49 | BIMK132 | PAHANG | 11.2828
74128 | T1 | 49 | BIMK132 | PAHANG | 10.0526
74118 | T2 | 49 | BNTG132 | PAHANG | 11.3387
74118 | T1 | 49 | BNTG132 | PAHANG | 8.081
62133 | T2 | 49 | BWTN132 | P PINANG | 39.9982
62133 | T1 | 49 | BWTN132 | P PINANG | 38.7007
62133 | T5 | 49 | BWTN132 | P PINANG | 0
562137 | T4 | 49 | PRGS132 | P PINANG | 21.0061
562137 | T3 | 49 | PRGS132 | P PINANG | 21.0455
51130 | T2 | 49 | SRDR132 | WPKL | 27.9781
51130 | T1 | 49 | SRDR132 | WPKL | 27.8539
88120 | T4 | 49 | AMPG132 | WPKL | 42.4761
88120 | T3 | 49 | AMPG132 | WPKL | 42.5704
51028 | T2 | 49 | AHTM132 | SELANGOR | 44.3266
51028 | T1 | 49 | AHTM132 | SELANGOR | 43.4909
88177 | T2 | 49 | BJLL132 | SELANGOR | 39.4804
88177 | T1 | 49 | BJLL132 | SELANGOR | 39.4245
51062 | T4 | 49 | BLKG132 | SELANGOR | 41.9139
51062 | T3 | 49 | BLKG132 | SELANGOR | 42.6936
75112 | T5 | 48.9 | KBRU132 | KELANTAN | 24.9814
75112 | T3 | 48.9 | KBRU132 | KELANTAN | 24.9265
75112 | T1 | 48.9 | KBRU132 | KELANTAN | 25.5758
51082 | T2 | 48.9 | PJST132 | SELANGOR | 26.5481
51082 | T1 | 48.9 | PJST132 | SELANGOR | 26.5398
97167 | T2 | 48.9 | PGTC132 | JOHOR | 47.6754
97167 | T1 | 48.9 | PGTC132 | JOHOR | 47.8349
97123 | T2 | 48.9 | PGIE132 | JOHOR | 13.8715
97123 | T1 | 48.9 | PGIE132 | JOHOR | 13.8622
97123 | T3 | 48.9 | PGIE132 | JOHOR | 12.4343
88174 | T2 | 48.9 | PCHJ132 | SELANGOR | 30.6476
88174 | T1 | 48.9 | PCHJ132 | SELANGOR | 30.6073
51025 | T2 | 48.9 | NSDA132 | SELANGOR | 31.0919
51025 | T1 | 48.9 | NSDA132 | SELANGOR | 31.0536
88173 | T2 | 48.9 | SDAM132 | WPKL | 27.6488
88173 | T1 | 48.9 | SDAM132 | WPKL | 27.8943
51091 | T2 | 48.9 | NSPK132 | SELANGOR | 25.7756
51091 | T1 | 48.9 | NSPK132 | SELANGOR | 26.3079
51050 | T2 | 48.9 | SRDN132 | WPKL | 24.2006
51050 | T1 | 48.9 | SRDN132 | WPKL | 24.2483
96150 | T2 | 48.9 | SDYN132 | NS | 45.0318
96150 | T1 | 48.9 | SDYN132 | NS | 44.7532
96134 | T2 | 48.9 | LKUT132 | NS | 10
96134 | T1 | 48.9 | LKUT132 | NS | 12.0335
74106 | T2 | 48.9 | TGLN132 | PAHANG | 5.2148
74106 | T1 | 48.9 | TGLN132 | PAHANG | 5.9562
74106 | T3 | 48.9 | TGLN132 | PAHANG | 11.2642
#N/A | T2 | 48.8 | KSTR132 | #N/A | #N/A
#N/A | T1 | 48.8 | KSTR132 | #N/A | #N/A
51031 | T2 | 48.8 | KCPK132 | SELANGOR | 31.0246
51031 | T1 | 48.8 | KCPK132 | SELANGOR | 31.1292
51200 | T2 | 48.8 | NRWG132 | SELANGOR | 37.5762
51200 | T1 | 48.8 | NRWG132 | SELANGOR | 37.6476
51045 | T4 | 48.8 | BKPR132 | SELANGOR | 38.7432
51045 | T3 | 48.8 | BKPR132 | SELANGOR | 38.7349
51084 | T2 | 48.8 | TMSY132 | SELANGOR | 15.4766
51084 | T1 | 48.8 | TMSY132 | SELANGOR | 15.5138
96144 | T2 | 48.8 | TKMG132 | NS | 6.827
96144 | T1 | 48.8 | TKMG132 | NS | 6.8529
96147 | T2 | 48.8 | PPJG132 | MELAKA | 10.589
96147 | T1 | 48.8 | PPJG132 | MELAKA | 0
96173 | T6 | 48.8 | MTNH132 | MELAKA | 11.4733
96173 | T5 | 48.8 | MTNH132 | MELAKA | 11.3801
#N/A | T4 | 48.8 | MTNH132 | #N/A | #N/A
96173 | T3 | 48.8 | MTNH132 | MELAKA | 2.8093
96173 | T2 | 48.8 | MTNH132 | MELAKA | 6.2451
96173 | T1 | 48.8 | MTNH132 | MELAKA | 6.2285
96135 | T4 | 48.8 | TJID132 | NS | 19.9893
96135 | T3 | 48.8 | TJID132 | NS | 19.9675
96135 | T2 | 48.8 | TJID132 | NS | 7.8615
96135 | T1 | 48.8 | TJID132 | NS | 11.1275
96129 | T2 | 48.8 | TTJF132 | NS | 14.9029
96129 | T1 | 48.8 | TTJF132 | NS | 14.8677
96193 | T5 | 48.8 | SSUN132 | NS | 0
96193 | T4 | 48.8 | SSUN132 | NS | 0
96193 | T3 | 48.8 | SSUN132 | NS | 0
596193 | T2 | 48.8 | SSUN132 | NS | 19.2717
596193 | T1 | 48.8 | SSUN132 | NS | 18.5282
96190 | T2 | 48.8 | STRA132 | NS | 6.9969
96190 | T1 | 48.8 | STRA132 | NS | 13.0794
74120 | T2 | 48.8 | BNTA132 | PAHANG | 2.7896
74120 | T1 | 48.8 | BNTA132 | PAHANG | 2.7813
74121 | T4 | 48.8 | KLIP132 | PAHANG | 12.4798
74121 | T3 | 48.8 | KLIP132 | PAHANG | 12.9841
74121 | T2 | 48.8 | KLIP132 | PAHANG | 5.9976
74121 | T1 | 48.8 | KLIP132 | PAHANG | 11.407
74123 | T7 | 48.8 | JNKA132 | PAHANG | 5.542
74123 | T2 | 48.8 | JNKA132 | PAHANG | 12.6745
74123 | T1 | 48.8 | JNKA132 | PAHANG | 12.5948
74122 | T2 | 48.8 | JTUT132 | PAHANG | 18.9921
74122 | T1 | 48.8 | JTUT132 | PAHANG | 19.1629
74151 | T4 | 48.8 | RBDR132 | PAHANG | 0
74151 | T3 | 48.8 | RBDR132 | PAHANG | 0
74151 | T2 | 48.8 | RBDR132 | PAHANG | 11.0332
74151 | T1 | 48.8 | RBDR132 | PAHANG | 11.7011
62105 | T4 | 48.8 | ATJN132 | P PINANG | 23.0864
62105 | T3 | 48.8 | ATJN132 | P PINANG | 22.4579
61109 | T2 | 48.8 | GRUN132 | KEDAH | 4.6991
61109 | T1 | 48.8 | GRUN132 | KEDAH | 4.7177
61107 | T2 | 48.8 | JENG132 | KEDAH | 13.914
61107 | T1 | 48.8 | JENG132 | KEDAH | 14.4773
63129 | T2 | 48.7 | LMUT132 | PERAK | 43.2455
63129 | T1 | 48.7 | LMUT132 | PERAK | 42.3395
63131 | T4 | 48.7 | LMTM132 | PERAK | 39.8843
63131 | T3 | 48.7 | LMTM132 | PERAK | 41.5587
88129 | T2 | 48.7 | MDAM132 | WPKL | 17.3322
88129 | T1 | 48.7 | MDAM132 | WPKL | 18.2683
88194 | T4 | 48.7 | BCVS132 | SELANGOR | 43.8937
88194 | T3 | 48.7 | BCVS132 | SELANGOR | 43.4019
97119 | T2 | 48.7 | PRJA132 | JOHOR | 0
97119 | T1 | 48.7 | PRJA132 | JOHOR | 20.4677
96405 | T4 | 48.7 | MCOP132 | MELAKA | 37.7336
96405 | T3 | 48.7 | MCOP132 | MELAKA | 37.6735
96405 | T2 | 48.7 | MCOP132 | MELAKA | 10.4834
96405 | T1 | 48.7 | MCOP132 | MELAKA | 13.2057
96124 | F2 | 48.7 | XNYI132 | MELAKA | 27.8171
96124 | F1 | 48.7 | XNYI132 | MELAKA | 9.9734
97117 | T2 | 48.7 | TKID132 | MELAKA | 8.3958
97117 | T1 | 48.7 | TKID132 | MELAKA | 8.4725
97128 | T4 | 48.7 | TKAK132 | JOHOR | 11.2041
97128 | T3 | 48.7 | TKAK132 | JOHOR | 11.1461
97150 | T2 | 48.7 | JMTH132 | JOHOR | 7.5384
97150 | T1 | 48.7 | JMTH132 | JOHOR | 6.389
97141 | T2 | 48.7 | SGMT132 | JOHOR | 9.8466
97141 | T1 | 48.7 | SGMT132 | JOHOR | 7.9878
97182 | T4 | 48.7 | BSPT132 | JOHOR | 15.5418
97182 | T3 | 48.7 | BSPT132 | JOHOR | 15.3606
97182 | T2 | 48.7 | BSPT132 | JOHOR | 9.7906
97182 | T1 | 48.7 | BSPT132 | JOHOR | 9.7761
97174 | T2 | 48.7 | BKPG132 | JOHOR | 3.8427
97174 | T1 | 48.7 | BKPG132 | JOHOR | 3.8365
97148 | T4 | 48.7 | CAAH132 | JOHOR | 9.9108
97148 | T3 | 48.7 | CAAH132 | JOHOR | 9.9708
96138 | T4 | 48.7 | BAHA132 | NS | 5.4674
96138 | T3 | 48.7 | BAHA132 | NS | 5.4177
96138 | T2 | 48.7 | BAHA132 | NS | 12.3835
96138 | T1 | 48.7 | BAHA132 | NS | 12.4001
96151 | T2 | 48.7 | NSCI132 | NS | 13.5692
96151 | T1 | 48.7 | NSCI132 | NS | 12.6745
96113 | T4 | 48.7 | UPSR132 | MELAKA | 25.6421
96113 | T3 | 48.7 | UPSR132 | MELAKA | 25.6545
96113 | T2 | 48.7 | UPSR132 | MELAKA | 11.6318
96113 | T1 | 48.7 | UPSR132 | MELAKA | 7.2423
96125 | T2 | 48.7 | NLAI132 | NS | 5.0035
96125 | T1 | 48.7 | NLAI132 | NS | 9.9377
51048 | T3 | 48.7 | BTGA132 | SELANGOR | 0
51048 | T2 | 48.7 | BTGA132 | SELANGOR | 19.0863
51048 | T1 | 48.7 | BTGA132 | SELANGOR | 18.814
51035 | T2 | 48.7 | BBDG132 | SELANGOR | 27.6499
51035 | T1 | 48.7 | BBDG132 | SELANGOR | 27.7327
51052 | T2 | 48.7 | RSID132 | SELANGOR | 16.3112
51052 | T2 | 48.7 | RSID132 | SELANGOR | 16.3112
97105 | T2 | 48.6 | GRSK132 | JOHOR | 11.9807
97105 | T1 | 48.6 | GRSK132 | JOHOR | 12.0087
97132 | T2 | 48.6 | KPTR132 | JOHOR | 11.7488
97132 | T1 | 48.6 | KPTR132 | JOHOR | 11.7539
97113 | T8 | 48.6 | SDAI132 | JOHOR | 0.6741
97113 | T7 | 48.6 | SDAI132 | JOHOR | 0.6275
97185 | T2 | 48.6 | LKIN132 | JOHOR | 11.7995
97185 | T1 | 48.6 | LKIN132 | JOHOR | 11.7415
74127 | T2 | 48.6 | SONG132 | PAHANG | 7.612
74127 | T1 | 48.6 | SONG132 | PAHANG | 14.467
74117 | T2 | 48.6 | MTKB132 | PAHANG | 22.578
74117 | T1 | 48.6 | MTKB132 | PAHANG | 0
74144 | T4 | 48.6 | TMID132 | PAHANG | 0
74144 | T3 | 48.6 | TMID132 | PAHANG | 0
74144 | T2 | 48.6 | TMID132 | PAHANG | 9.1155
74144 | T1 | 48.6 | TMID132 | PAHANG | 9.0399
74147 | F1 | 48.6 | MNID132 | PAHANG | 0.321
62118 | T3 | 48.6 | GLGR132 | P PINANG | 21.4069
62118 | T2 | 48.6 | GLGR132 | P PINANG | 21.3737
62118 | T1 | 48.6 | GLGR132 | P PINANG | 19.1961
62110 | T2 | 48.6 | BMTR132 | P PINANG | 57.494
62110 | T1 | 48.6 | BMTR132 | P PINANG | 62.7419
62120 | T2 | 48.6 | BKWS132 | P PINANG | 54.3657
62120 | T1 | 48.6 | BKWS132 | P PINANG | 55.8776
61137 | T4 | 48.6 | KGAR132 | PERLIS | 10.9504
61137 | T3 | 48.6 | KGAR132 | PERLIS | 7.408
51041 | T4 | 48.6 | SHAW132 | SELANGOR | 28.4565
51041 | T3 | 48.6 | SHAW132 | SELANGOR | 28.5911
51041 | T2 | 48.6 | SHAW132 | SELANGOR | 5.8288
51041 | T1 | 48.6 | SHAW132 | SELANGOR | 9.2294
51051 | T4 | 48.6 | TPGR132 | SELANGOR | 45.5454
51051 | T3 | 48.6 | TPGR132 | SELANGOR | 45.2886
51003 | T3 | 48.6 | SHAN132 | SELANGOR | 0
51003 | T2 | 48.6 | SHAN132 | SELANGOR | 0.007
51003 | T1 | 48.6 | SHAN132 | SELANGOR | 0
51002 | T2 | 48.6 | SHLB132 | SELANGOR | 27.5132
51002 | T1 | 48.6 | SHLB132 | SELANGOR | 27.4096
51037 | T2 | 48.6 | BBTC132 | SELANGOR | 38.0753
51037 | T1 | 48.6 | BBTC132 | SELANGOR | 38.708
61115 | T2 | 48.6 | BDNG132 | KEDAH | 18.7487
61115 | T1 | 48.6 | BDNG132 | KEDAH | 21.703
88111 | T2 | 48.6 | KULN132 | WPKL | 38.2026
88111 | T1 | 48.6 | KULN132 | WPKL | 38.272
75103 | T2 | 48.6 | DGUN132 | TGANU | 5.1723
75103 | T1 | 48.6 | DGUN132 | TGANU | 5.2179
75109 | T2 | 48.6 | CHRG132 | TGANU | 14.3209
75109 | T1 | 48.6 | CHRG132 | TGANU | 17.8064
97109 | T2 | 48.5 | KLUG132 | JOHOR | 8.2529
97109 | T1 | 48.5 | KLUG132 | JOHOR | 8.5646
97115 | T2 | 48.5 | MAJD132 | JOHOR | 6.2513
97115 | T1 | 48.5 | MAJD132 | JOHOR | 6.5547
75118 | T2 | 48.5 | DGID132 | TGANU | 25.8719
75118 | T1 | 48.5 | DGID132 | TGANU | 0
75144 | T2 | 48.5 | CKAI132 | TGANU | 12.7594
75144 | T1 | 48.5 | CKAI132 | TGANU | 12.7325
61132 | T4 | 48.5 | PAUH132 | KEDAH | 10.8261
61132 | T3 | 48.5 | PAUH132 | KEDAH | 10.7723
62108 | T4 | 48.5 | BMYK132 | P PINANG | 48.2977
62108 | T3 | 48.5 | BMYK132 | P PINANG | 49.2069
62108 | T2 | 48.5 | BMYK132 | P PINANG | 14.6306
62108 | T1 | 48.5 | BMYK132 | P PINANG | 11.9517
62155 | T4 | 48.5 | PRID132 | P PINANG | 36.9093
62155 | T3 | 48.5 | PRID132 | P PINANG | 36.8203
62155 | T2 | 48.5 | PRID132 | P PINANG | 23.4313
62155 | T1 | 48.5 | PRID132 | P PINANG | 23.6135
51103 | T3 | 48.5 | PCHP132 | SELANGOR | 25.6452
551103 | T2 | 48.5 | PCHP132 | SELANGOR | 46.3707
551103 | T1 | 48.5 | PCHP132 | SELANGOR | 46.1988
51006 | T4 | 48.5 | CBPS132 | SELANGOR | 44.1744
51006 | T3 | 48.5 | CBPS132 | SELANGOR | 44.9676
51027 | T2 | 48.5 | SHAB132 | SELANGOR | 26.0252
51027 | T1 | 48.5 | SHAB132 | SELANGOR | 25.2341
88122 | T2 | 48.5 | SGBT132 | WPKL | 39.6472
88122 | T1 | 48.5 | SGBT132 | WPKL | 40.1111
75206 | T2 | 48.5 | JELI275 | KELANTAN | 6.1705
75206 | T1 | 48.5 | JELI275 | KELANTAN | 6.3818
75114 | T2 | 48.5 | PPTH132 | KELANTAN | 19.1226
75114 | T1 | 48.5 | PPTH132 | KELANTAN | 19.6103
75106 | T5 | 48.5 | SJTH132 | KELANTAN | 14.8915
75106 | T2 | 48.5 | SJTH132 | KELANTAN | 21.5291
75106 | T1 | 48.5 | SJTH132 | KELANTAN | 21.3261
96195 | T2 | 48.4 | ZRNA132 | MELAKA | 6.7473
96195 | T1 | 48.4 | ZRNA132 | MELAKA | 6.7297
96181 | F3 | 48.4 | SPWR132 | MELAKA | 3.321
96181 | F2 | 48.4 | SPWR132 | MELAKA | 2.321
96181 | F1 | 48.4 | SPWR132 | MELAKA | 1.321
96191 | T4 | 48.4 | CHNG132 | MELAKA | 31.8509
96191 | T3 | 48.4 | CHNG132 | MELAKA | 31.8406
96191 | T2 | 48.4 | CHNG132 | MELAKA | 10.6045
96191 | T1 | 48.4 | CHNG132 | MELAKA | 7.3438
96111 | T2 | 48.4 | BMKA132 | MELAKA | 8.8483
96111 | T1 | 48.4 | BMKA132 | MELAKA | 5.6828
96108 | T2 | 48.4 | MMKA132 | MELAKA | 7.0093
96108 | T1 | 48.4 | MMKA132 | MELAKA | 9.3723
96122 | T2 | 48.4 | BVTA132 | MELAKA | 8.5501
96122 | T1 | 48.4 | BVTA132 | MELAKA | 3.3695
96189 | T4 | 48.4 | TGBU132 | MELAKA | 16.861
96189 | T3 | 48.4 | TGBU132 | MELAKA | 16.7823
96189 | T2 | 48.4 | TGBU132 | MELAKA | 3.6387
96189 | T1 | 48.4 | TGBU132 | MELAKA | 3.7268
96197 | F2 | 48.4 | PPSR132 | MELAKA | 0.1243
96197 | F1 | 48.4 | PPSR132 | MELAKA | 2.7441
96196 | F1 | 48.4 | HLNM132 | MELAKA | 9.539
96101 | T4 | 48.4 | BRBI132 | MELAKA | 10.1313
96101 | T3 | 48.4 | BRBI132 | MELAKA | 10.1531
96101 | T2 | 48.4 | BRBI132 | MELAKA | 9.1227
96101 | T1 | 48.4 | BRBI132 | MELAKA | 6.6624
75116 | T4 | 48.4 | GBDK132 | TGANU | 19.4291
75116 | T3 | 48.4 | GBDK132 | TGANU | 19.3752
75116 | T2 | 48.4 | GBDK132 | TGANU | 10.6832
75116 | T1 | 48.4 | GBDK132 | TGANU | 10.6625
75140 | T4 | 48.4 | KBRG132 | TGANU | 5.133
75140 | T3 | 48.4 | KBRG132 | TGANU | 5.0563
75140 | T2 | 48.4 | KBRG132 | TGANU | 10.4865
75140 | T1 | 48.4 | KBRG132 | TGANU | 10.8862
75115 | T4 | 48.4 | KTGU132 | TGANU | 11.5365
75115 | T3 | 48.4 | KTGU132 | TGANU | 11.521
75115 | T2 | 48.4 | KTGU132 | TGANU | 11.4909
75115 | T1 | 48.4 | KTGU132 | TGANU | 13.361
75138 | T3 | 48.4 | BRKT132 | TGANU | 14.7041
75138 | T2 | 48.4 | BRKT132 | TGANU | 9.0182
75138 | T1 | 48.4 | BRKT132 | TGANU | 9.1207
97143 | T4 | 48.4 | SLNG132 | JOHOR | 29.0064
97143 | T3 | 48.4 | SLNG132 | JOHOR | 29.1514
97143 | T2 | 48.4 | SLNG132 | JOHOR | 13.5661
97143 | T1 | 48.4 | SLNG132 | JOHOR | 12.4767
97162 | T4 | 48.4 | SNAI132 | JOHOR | 42.6719
97162 | T3 | 48.4 | SNAI132 | JOHOR | 43.0695
97162 | T2 | 48.4 | SNAI132 | JOHOR | 9.6229
97162 | T1 | 48.4 | SNAI132 | JOHOR | 9.6219
97112 | T1 | 48.4 | KLAI132 | JOHOR | 0
597112 | T2 | 48.4 | KLAI132R | JOHOR | 20.1353
97159 | F1 | 48.4 | UTMJ132 | JOHOR | 4.0799
597159 | F2 | 48.4 | UTMJ132R | JOHOR | 1.3565
51001 | T2 | 48.4 | BTAI132 | SELANGOR | 0
51001 | T1 | 48.4 | BTAI132 | SELANGOR | 11.8761
588124 | T2 | 48.4 | KULE132 | WPKL | 39.3707
588124 | T1 | 48.4 | KULE132 | WPKL | 39.3697
88163 | T2 | 48.4 | KLPV132 | WPKL | 28.6108
88163 | T1 | 48.4 | KLPV132 | WPKL | 28.5694
61112 | T2 | 48.4 | TKBU132 | KEDAH | 31.707
61112 | T1 | 48.4 | TKBU132 | KEDAH | 31.6376
#N/A | T3 | 48.3 | TPOI132 | #N/A | #N/A
97127 | T2 | 48.3 | TPOI132 | JOHOR | 11.9165
97127 | T1 | 48.3 | TPOI132 | JOHOR | 11.9093
97129 | T2 | 48.3 | BPHT132 | JOHOR | 11.8906
97129 | T1 | 48.3 | BPHT132 | JOHOR | 11.055
97121 | T2 | 48.3 | TPCH132 | JOHOR | 4.8668
97121 | T1 | 48.3 | TPCH132 | JOHOR | 11.4329
97107 | T2 | 48.3 | YGPG132 | JOHOR | 9.8683
97107 | T1 | 48.3 | YGPG132 | JOHOR | 11.4443
51057 | T4 | 48.3 | MERU132 | SELANGOR | 44.0532
51057 | T3 | 48.3 | MERU132 | SELANGOR | 43.9352
51009 | T3 | 48.3 | PROT132 | SELANGOR | 49.7164
51009 | T2 | 48.3 | PROT132 | SELANGOR | 32.2796
51009 | T1 | 48.3 | PROT132 | SELANGOR | 32.4039
96132 | T2 | 48.3 | KLAT132 | NS | 9.5856
96132 | T1 | 48.3 | KLAT132 | NS | 13.7411
61103 | T2 | 48.3 | TEWA132 | LANGKAWI | 33.2882
61103 | T1 | 48.3 | TEWA132 | LANGKAWI | 0
61125 | T4 | 48.3 | UMKA132 | LANGKAWI | 17.1541
61125 | T3 | 48.3 | UMKA132 | LANGKAWI | 17.299
61125 | T2 | 48.3 | UMKA132 | LANGKAWI | 3.7237
61125 | T1 | 48.3 | UMKA132 | LANGKAWI | 3.7268
561145 | F2 | 48.3 | KCMT132R | LANGKAWI | 26.1764
61145 | F1 | 48.3 | KCMT132 | LANGKAWI | 0
88161 | T5 | 48.3 | IMBI132 | WPKL | 33.9478
88161 | T4 | 48.3 | IMBI132 | WPKL | 25.6182
88161 | T3 | 48.3 | IMBI132 | WPKL | 25.4443
51011 | T5 | 48.3 | KDSA132 | SELANGOR | 40.8152
51011 | T4 | 48.3 | KDSA132 | SELANGOR | 39.992
51011 | T3 | 48.3 | KDSA132 | SELANGOR | 51.0346
88133 | T2 | 48.3 | GWAY132 | WPKL | 13.302
88133 | T1 | 48.3 | GWAY132 | WPKL | 13.3186
62126 | F2 | 48.3 | JNKO132 | P PINANG | 0.0332
62126 | F1 | 48.3 | JNKO132 | P PINANG | 0.3334
62122 | T2 | 48.3 | VDOR132 | P PINANG | 15.5097
62122 | T1 | 48.3 | VDOR132 | P PINANG | 12.69
63118 | T2 | 48.3 | PBTR132 | PERAK | 22.1845
63118 | T1 | 48.3 | PBTR132 | PERAK | 19.1557
62111 | T2 | 48.3 | NTBL132 | P PINANG | 14.8252
62111 | T1 | 48.3 | NTBL132 | P PINANG | 11.9238
62135 | T2 | 48.2 | SPNG132 | P PINANG | 25.9372
62135 | T1 | 48.2 | SPNG132 | P PINANG | 27.4583
51060 | T2 | 48.2 | BHGT132 | SELANGOR | 9.627
51060 | T1 | 48.2 | BHGT132 | SELANGOR | 5.6238
96152 | T4 | 48.2 | AMID132 | NS | 31.6034
96152 | T3 | 48.2 | AMID132 | NS | 31.9555
96152 | T2 | 48.2 | AMID132 | NS | 7.4691
96152 | T1 | 48.2 | AMID132 | NS | 6.7225
96156 | T4 | 48.2 | MTIN132 | NS | 19.9934
96156 | T3 | 48.2 | MTIN132 | NS | 0
96188 | T4 | 48.2 | PJAM132 | NS | 2.9615
96188 | T3 | 48.2 | PJAM132 | NS | 2.7751
96188 | T2 | 48.2 | PJAM132 | NS | 7.1501
96188 | T1 | 48.2 | PJAM132 | NS | 7.5716
51092 | T2 | 48.2 | KEST132 | WPKL | 45.7483
51092 | T1 | 48.2 | KEST132 | WPKL | 45.9347
51054 | T2 | 48.2 | SMYH132 | SELANGOR | 12.1516
51054 | T1 | 48.2 | SMYH132 | SELANGOR | 8.4383
51053 | T6 | 48.2 | BRNG132 | SELANGOR | 33.6754
51053 | T5 | 48.2 | BRNG132 | SELANGOR | 34.0006
51053 | T2 | 48.2 | BRNG132 | SELANGOR | 19.6879
51053 | T1 | 48.2 | BRNG132 | SELANGOR | 0
88114 | T2 | 48.2 | BMKM132 | WPKL | 14.1749
88114 | T1 | 48.2 | BMKM132 | WPKL | 14.1749
97116 | T4 | 48.2 | KTGI132 | JOHOR | 5.8112
97116 | T3 | 48.2 | KTGI132 | JOHOR | 8.3233
97188 | T4 | 48.2 | UTRM132 | JOHOR | 29.6836
97188 | T3 | 48.2 | UTRM132 | JOHOR | 30.5555
97188 | T2 | 48.2 | UTRM132 | JOHOR | 9.3102
97188 | T1 | 48.2 | UTRM132 | JOHOR | 9.2791
97118 | T2 | 48.2 | PUBB132 | JOHOR | 10.2514
97118 | T1 | 48.2 | PUBB132 | JOHOR | 10.1582
97198 | T2 | 48.2 | PLGI132 | JOHOR | 29.2052
97198 | T1 | 48.2 | PLGI132 | JOHOR | 29.0561
97111 | T2 | 48.2 | RNGM132 | JOHOR | 4.4765
97111 | T1 | 48.2 | RNGM132 | JOHOR | 4.3905
97149 | T4 | 48.2 | KLID132 | JOHOR | 10.1158
97149 | T3 | 48.2 | KLID132 | JOHOR | 6.3331
97149 | T2 | 48.2 | KLID132 | JOHOR | 10.852
97149 | T1 | 48.2 | KLID132 | JOHOR | 10.1261
97131 | T4 | 48.2 | MSNG132 | JOHOR | 6.8291
97131 | T3 | 48.2 | MSNG132 | JOHOR | 6.8384
97131 | T2 | 48.2 | MSNG132 | JOHOR | 3.8686
97131 | T1 | 48.2 | MSNG132 | JOHOR | 2.8311
74133 | T2 | 48.2 | TGMK132 | PAHANG | 13.7411
74133 | T1 | 48.2 | TGMK132 | PAHANG | 13.7514
97138 | T2 | 48.2 | NYOR132 | JOHOR | 16.6104
97138 | T1 | 48.2 | NYOR132 | JOHOR | 11.3926
61137 | T2 | 48.1 | KGAR132 | PERLIS | 11.7281
61137 | T1 | 48.1 | KGAR132 | PERLIS | 12.0377
63111 | T4 | 48.1 | SIKD132 | PERAK | 23.9211
63111 | T3 | 48.1 | SIKD132 | PERAK | 23.8703
51085 | T4 | 48.1 | LKDG132 | SELANGOR | 28.47
51085 | T3 | 48.1 | LKDG132 | SELANGOR | 28.645
51075 | T2 | 48.1 | SJTC132 | SELANGOR | 28.5301
51075 | T1 | 48.1 | SJTC132 | SELANGOR | 28.4607
62131 | T2 | 48.1 | BBRU132 | P PINANG | 48.1662
62131 | T1 | 48.1 | BBRU132 | P PINANG | 48.453
96133 | T2 | 48.1 | SMRK132 | NS | 10.8013
96133 | T1 | 48.1 | SMRK132 | NS | 11.5406
96194 | F4 | 48.1 | HLNN132 | NS | 0
96194 | F3 | 48.1 | HLNN132 | NS | 10.8686
96194 | F2 | 48.1 | HLNN132 | NS | 10.7143
96194 | F1 | 48.1 | HLNN132 | NS | 0.1118
97142 | T2 | 48.1 | SELG132 | JOHOR | 14.6927
97142 | T1 | 48.1 | SELG132 | JOHOR | 14.6927
97152 | T2 | 48.1 | STUL132 | JOHOR | 5.2779
97152 | T1 | 48.1 | STUL132 | JOHOR | 5.2914
97146 | T4 | 48.1 | SGAD132 | JOHOR | 10.7537
97146 | T3 | 48.1 | SGAD132 | JOHOR | 11.9062
97146 | T2 | 48.1 | SGAD132 | JOHOR | 8.7023
97146 | T1 | 48.1 | SGAD132 | JOHOR | 15.2177
97103 | T4 | 48.1 | PJML132 | JOHOR | 9.5804
97103 | T3 | 48.1 | PJML132 | JOHOR | 9.6156
97104 | T2 | 48.1 | PYSF132 | JOHOR | 3.9867
97104 | T1 | 48.1 | PYSF132 | JOHOR | 4.0208
97120 | T2 | 48.1 | PSRI132 | JOHOR | 16.16
97120 | T1 | 48.1 | PSRI132 | JOHOR | 6.8032
97125 | T4 | 48.1 | SSLG132 | JOHOR | 4.5106
97125 | T3 | 48.1 | SSLG132 | JOHOR | 4.5013

## Working tab (ref) (hidden)
Assigned Feeders | CB | MW Quantum 2024 | MW Quantum 2025 | Load Area Affected | UFLS DYR | [5 empty] | Load (PSSE) | PSSE | [5 empty] | PSSE (reference)
132/22kV T1 & T2 | 1T0 & 2T0 | 21.3659 |  | CBRU 22kV | 97178 | T2 | 49.2 | CBRU132 | CBRU132T2 | JOHOR | 8.9519 | 63177 | AYTH132 132.00 | T7 | AYTH132 | AYTH132T7 | 11.6897 | AYTH132 132.00 | T7 | AYTH132 | AYTH132T7 | 11.6897 | 63177 | CBRU132T2
132/22kV T1 & T2 | 1T0 & 2T0 | 21.8789 |  | PGDT 22kV | 97178 | T1 | 49.2 | CBRU132 | CBRU132T1 | JOHOR | 8.9871 | 61123 | BKRS132 132.00 | T1 | BKRS132 | BKRS132T1 | 21.2899 | BKRS132 132.00 | T1 | BKRS132 | BKRS132T1 | 21.2899 | 61123 | CBRU132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 64.0768 |  | TMPI 33kV | 97153 | T2 | 49.2 | PGDT132 | PGDT132T2 | JOHOR | 10.1427 | 61123 | BKRS132 132.00 | T2 | BKRS132 | BKRS132T2 | 21.207 | BKRS132 132.00 | T2 | BKRS132 | BKRS132T2 | 21.207 | 61123 | PGDT132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 41.5461 |  | SARA 33kV | 97153 | T1 | 49.2 | PGDT132 | PGDT132T1 | JOHOR | 2.4873 | 51089 | CBJC132 132.00 | T1 | CBJC132 | CBJC132T1 | 27.6561 | CBJC132 132.00 | T1 | CBJC132 | CBJC132T1 | 27.6561 | 51089 | PGDT132T1
132/33kV T1 & T2 | 1T0 & 2T1 | 18.5562 |  | PKNI 33kV | 97192 | T2 | 49.2 | TMPI132 | TMPI132T2 | JOHOR | 27.9139 | 96176 | CMBG132 132.00 | T3 | CMBG132 | CMBG132T3 | 18.4629 | CMBG132 132.00 | T3 | CMBG132 | CMBG132T3 | 18.4629 | 96176 | TMPI132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 15.3861 |  | HPGH 33kV | 97192 | T1 | 49.2 | TMPI132 | TMPI132T1 | JOHOR | 29.0913 | 61101 | CPNG132 132.00 | T1 | CPNG132 | CPNG132T1 | 5.7418 | CPNG132 132.00 | T1 | CPNG132 | CPNG132T1 | 5.7418 | 61101 | TMPI132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 36.4197 |  | ESTK 33kV | 62128 | T2 | 49.2 | SARA132 | SARA132T2 | P PINANG | 35.7174 | 61101 | CPNG132 132.00 | T2 | CPNG132 | CPNG132T2 | 5.7594 | CPNG132 132.00 | T2 | CPNG132 | CPNG132T2 | 5.7594 | 61101 | SARA132T2
132/11kV T1 & T2 | 30 & 32 | 20.2233 |  | KRPH 11kV | 62128 | T1 | 49.2 | SARA132 | SARA132T1 | P PINANG | 35.6077 | 61137 | KGAR132 132.00 | T1 | KGAR132 | KGAR132T1 | 12.0377 | KGAR132 132.00 | T1 | KGAR132 | KGAR132T1 | 12.0377 | 61137 | SARA132T1
132/11kV T1 & T2 | 31 & 32 | 21.5372 |  | PKID 11kV | 74115 | T2 | 49.2 | PKNI132 | PKNI132T2 | PAHANG | 6.3124 | 61137 | KGAR132 132.00 | T2 | KGAR132 | KGAR132T2 | 11.7281 | KGAR132 132.00 | T2 | KGAR132 | KGAR132T2 | 11.7281 | 61137 | PKNI132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 25.2821 |  | PKID 33kV | 74115 | T1 | 49.2 | PKNI132 | PKNI132T1 | PAHANG | 6.2824 | 61137 | KGAR132 132.00 | T3 | KGAR132 | KGAR132T3 | 7.408 | KGAR132 132.00 | T3 | KGAR132 | KGAR132T3 | 7.408 | 61137 | PKNI132T1
132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 61.5771 |  | KVRT 33 kV | 96106 | T2 | 49.2 | HPGH132 | HPGH132T2 | MELAKA | 6.0111 | 61137 | KGAR132 132.00 | T4 | KGAR132 | KGAR132T4 | 10.9504 | KGAR132 132.00 | T4 | KGAR132 | KGAR132T4 | 10.9504 | 61137 | HPGH132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 83.9211 |  | MLBU 33kV | 96106 | T1 | 49.2 | HPGH132 | HPGH132T1 | MELAKA | 5.9893 | 61102 | KPLS132 132.00 | T1 | KPLS132 | KPLS132T1 | 9.0347 | KPLS132 132.00 | T1 | KPLS132 | KPLS132T1 | 9.0347 | 61102 | HPGH132T1
132/33kV T1 & T2 | 1T0 & 2T1 | 76.0234 |  | STIA 33kV | 96169 | T2 | 49.2 | ESTK132 | ESTK132T2 | SELANGOR | 22.8441 | 61102 | KPLS132 132.00 | T2 | KPLS132 | KPLS132T2 | 8.9167 | KPLS132 132.00 | T2 | KPLS132 | KPLS132T2 | 8.9167 | 61102 | ESTK132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 28.4475 |  | DCTY 33kV | 96169 | T1 | 49.2 | ESTK132 | ESTK132T1 | SELANGOR | 22.637 | 96116 | PMKA132 132.00 | T1 | PMKA132 | PMKA132T1 | 4.1555 | PMKA132 132.00 | T1 | PMKA132 | PMKA132T1 | 4.1555 | 96116 | ESTK132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 89.8683 |  | MJLR 33kV | 63145 | T2 | 49.2 | PKID132 | PKID132T2 | PERAK | 9.6612 | 96116 | PMKA132 132.00 | T2 | PMKA132 | PMKA132T2 | 4.1555 | PMKA132 132.00 | T2 | PMKA132 | PMKA132T2 | 4.1555 | 96116 | PKID132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 71.0055 |  | SHMS 33kV | 63145 | T1 | 49.2 | PKID132 | PKID132T1 | PERAK | 5.4146 | 61148 | AJYA132 132.00 | T1 | AJYA132 | AJYA132T1 | 0 | AJYA132 132.00 | T1 | AJYA132 | AJYA132T1 | 0 | 61148 | PKID132T1
132/33kV T1 & T2 | 1T0 & 2T2 | 25.6995 |  | SCTY 33kV | 63145 | T4 | 49.2 | PKID132 | PKID132T4 | PERAK | 12.6579 | 61148 | AJYA132 132.00 | T2 | AJYA132 | AJYA132T2 | 16.3453 | AJYA132 132.00 | T2 | AJYA132 | AJYA132T2 | 16.3453 | 61148 | PKID132T4
132/33kV T1, T2 & T3 | 1T0 & 2T0 & 3T0 | 157.1371 |  | CJYA 33kV | 63145 | T3 | 49.2 | PKID132 | PKID132T3 | PERAK | 12.6652 | 61148 | AJYA132 132.00 | T3 | AJYA132 | AJYA132T3 | 20.0669 | AJYA132 132.00 | T3 | AJYA132 | AJYA132T3 | 20.0669 | 61148 | PKID132T3
132/33kV T3 & T4 | 3T0 & 4T0 | 60.7924 |  | DDSA 33kV | 63173 | T4 | 49.2 | KVRT132 | KVRT132T4 | PERAK | 33.9333 | 61148 | AJYA132 132.00 | T4 | AJYA132 | AJYA132T4 | 0 | AJYA132 132.00 | T4 | AJYA132 | AJYA132T4 | 0 | 61148 | KVRT132T4
132/11kV T1 & T2 | 31 & 32 | 17.2107 |  | MGON 11kV | 63173 | T3 | 49.2 | KVRT132 | KVRT132T3 | PERAK | 33.9395 | 61104 | ASTR132 132.00 | T1 | ASTR132 | ASTR132T1 | 5.9759 | ASTR132 132.00 | T1 | ASTR132 | ASTR132T1 | 5.9759 | 61104 | KVRT132T3
132/33kV T1 & T2 | 1T0 & 2T0 | 42.691 |  | PAUH 33kV | 63146 | T4 | 49.2 | MLBU132 | MLBU132T4 | PERAK | 34.6333 | 61104 | ASTR132 132.00 | T2 | ASTR132 | ASTR132T2 | 5.8444 | ASTR132 132.00 | T2 | ASTR132 | ASTR132T2 | 5.8444 | 61104 | MLBU132T4
132/33kV T3 & T4 | 3T0 & 4T0 | 22.3732 |  | TMOH 33kV | 63146 | T3 | 49.2 | MLBU132 | MLBU132T3 | PERAK | 34.4842 | 61104 | ASTR132 132.00 | T3 | ASTR132 | ASTR132T3 | 26.3037 | ASTR132 132.00 | T3 | ASTR132 | ASTR132T3 | 26.3037 | 61104 | MLBU132T3
132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 24.6724 |  | KLBG 33kV | 51013 | T2 | 49.2 | STIA132 | STIA132T2 | SELANGOR | 36.9797 | 61104 | ASTR132 132.00 | T4 | ASTR132 | ASTR132T4 | 12.719 | ASTR132 132.00 | T4 | ASTR132 | ASTR132T4 | 12.719 | 61104 | STIA132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 32.1433 |  | NKAN 33kV | 51013 | T1 | 49.2 | STIA132 | STIA132T1 | SELANGOR | 33.1173 | 61115 | BDNG132 132.00 | T1 | BDNG132 | BDNG132T1 | 21.703 | BDNG132 132.00 | T1 | BDNG132 | BDNG132T1 | 21.703 | 61115 | STIA132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 8.5343 |  | TASK 22kV | 88104 | T2 | 49.2 | DCTY132 | DCTY132T2 | WPKL | 12.9489 | 61115 | BDNG132 132.00 | T2 | BDNG132 | BDNG132T2 | 18.7487 | BDNG132 132.00 | T2 | BDNG132 | BDNG132T2 | 18.7487 | 61115 | DCTY132T2
132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 1W0 & 5T0 | 123.2475 |  | SPKC 33kV | 88104 | T1 | 49.2 | DCTY132 | DCTY132T1 | WPKL | 12.8951 | 61124 | BKHM132 132.00 | T1 | BKHM132 | BKHM132T1 | 6.0452 | BKHM132 132.00 | T1 | BKHM132 | BKHM132T1 | 6.0452 | 61124 | DCTY132T1
132/11kV T1 & T2 | 31 & 32 | 24.5161 |  | NUNI 11kV | 88128 | T2 | 49.2 | MJLR132 | MJLR132T2 | WPKL | 49.3467 | 61124 | BKHM132 132.00 | T2 | BKHM132 | BKHM132T2 | 6.0483 | BKHM132 132.00 | T2 | BKHM132 | BKHM132T2 | 6.0483 | 61124 | MJLR132T2
WA18 1 & 2 | H10 & H20 | - |  | TNB-Singapore Interconnection | 88128 | T1 | 49.2 | MJLR132 | MJLR132T1 | WPKL | 49.94 | 61124 | BKHM132 132.00 | T3 | BKHM132 | BKHM132T3 | 18.2548 | BKHM132 132.00 | T3 | BKHM132 | BKHM132T3 | 18.2548 | 61124 | MJLR132T1
132/22kV T1 & T2 | 1T0 & 2T0 | 29.3428 |  | TBRU 22kV | 88142 | T2 | 49.2 | SHMS132 | SHMS132T2 | WPKL | 28.1138 | 61124 | BKHM132 132.00 | T4 | BKHM132 | BKHM132T4 | 18.319 | BKHM132 132.00 | T4 | BKHM132 | BKHM132T4 | 18.319 | 61124 | SHMS132T2
KRYG 1 & 2 | 305 & 405 | 30 |  | KRYG | 88142 | T1 | 49.2 | SHMS132 | SHMS132T1 | WPKL | 28.2235 | 61120 | BSBU132 132.00 | T1 | BSBU132 | BSBU132T1 | 6.1395 | BSBU132 132.00 | T1 | BSBU132 | BSBU132T1 | 6.1395 | 61120 | SHMS132T1
SHEL 1 & 2 | 505 & 605 | 36 |  | SHELL | 88107 | T2 | 49.2 | SCTY132 | SCTY132T2 | WPKL | 17.0774 | 61120 | BSBU132 132.00 | T2 | BSBU132 | BSBU132T2 | 6.1125 | BSBU132 132.00 | T2 | BSBU132 | BSBU132T2 | 6.1125 | 61120 | SCTY132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 77.918 |  | HCOM 33 kV | 88107 | T1 | 49.2 | SCTY132 | SCTY132T1 | WPKL | 17.1303 | 61120 | BSBU132 132.00 | T3 | BSBU132 | BSBU132T3 | 0 | BSBU132 132.00 | T3 | BSBU132 | BSBU132T3 | 0 | 61120 | SCTY132T1
132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 72.8698 |  | SHAE 33kV | 51038 | T3 | 49.2 | CJYA132 | CJYA132T3 | SELANGOR | 66.9274 | 61120 | BSBU132 132.00 | T4 | BSBU132 | BSBU132T4 | 0 | BSBU132 132.00 | T4 | BSBU132 | BSBU132T4 | 0 | 61120 | CJYA132T3
132/33kV T1 & T2 | 1T0 & 2T0 | 64 |  | SHAS 33kV | 51038 | T2 | 49.2 | CJYA132 | CJYA132T2 | SELANGOR | 33.5056 | 61108 | GCPD132 132.00 | T1 | GCPD132 | GCPD132T1 | 6.242 | GCPD132 132.00 | T1 | GCPD132 | GCPD132T1 | 6.242 | 61108 | CJYA132T2
132/33kV T2 & T3 & T4 | 2T0, 3T0 & 4T0 | 67.9031 |  | PCOR 33kV | 51038 | T1 | 49.2 | CJYA132 | CJYA132T1 | SELANGOR | 31.8343 | 61108 | GCPD132 132.00 | T2 | GCPD132 | GCPD132T2 | 6.2492 | GCPD132 132.00 | T2 | GCPD132 | GCPD132T2 | 6.2492 | 61108 | CJYA132T1
132/11kV T1 & T2 | 31 & 32 | 20.2863 |  | JTGH 11kV | 88195 | T4 | 49.2 | DDSA132 | DDSA132T4 | WPKL | 30.6943 | 61116 | GRNE132 132.00 | T1 | GRNE132 | GRNE132T1 | 16.9304 | GRNE132 132.00 | T1 | GRNE132 | GRNE132T1 | 16.9304 | 61116 | DDSA132T4
132/33kV T1 & T2 | 1T0 & 2T0 | 74.3213 |  | SJAY 33kV | 88195 | T3 | 49.2 | DDSA132 | DDSA132T3 | WPKL | 30.6777 | 61116 | GRNE132 132.00 | T2 | GRNE132 | GRNE132T2 | 16.9325 | GRNE132 132.00 | T2 | GRNE132 | GRNE132T2 | 16.9325 | 61116 | DDSA132T3
132/33kV T3 & T4 | 3T0&4T0 | 51.9714 |  | INTN 33kV | 61119 | T2 | 49.2 | MGON132 | MGON132T2 | KEDAH | 8.2529 | 61109 | GRUN132 132.00 | T1 | GRUN132 | GRUN132T1 | 4.7177 | GRUN132 132.00 | T1 | GRUN132 | GRUN132T1 | 4.7177 | 61109 | MGON132T2
132/11kV T1 & T2 | 31&32 | 31.6547 |  | INTN 22kV | 61119 | T1 | 49.2 | MGON132 | MGON132T1 | KEDAH | 8.2591 | 61109 | GRUN132 132.00 | T2 | GRUN132 | GRUN132T2 | 4.6991 | GRUN132 132.00 | T2 | GRUN132 | GRUN132T2 | 4.6991 | 61109 | MGON132T1
132/11kV T1 & T2 | 31 & 32 | 9.404 |  | MPSS 11kV | 61132 | T2 | 49.2 | PAUH132 | PAUH132T2 | KEDAH | 18.9869 | 61131 | GTHR132 132.00 | T1 | GTHR132 | GTHR132T1 | 45.9937 | GTHR132 132.00 | T1 | GTHR132 | GTHR132T1 | 45.9937 | 61131 | PAUH132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 60 |  | TJUG 33kV | 61132 | T1 | 49.2 | PAUH132 | PAUH132T1 | KEDAH | 18.8088 | 61131 | GTHR132 132.00 | T2 | GTHR132 | GTHR132T2 | 45.768 | GTHR132 132.00 | T2 | GTHR132 | GTHR132T2 | 45.768 | 61131 | PAUH132T1
132/11kV T1 & T2 | 31 & 32 | 26.877 |  | MJYA 11kV | 63127 | T4 | 49.1 | TMOH132 | TMOH132T4 | PERAK | 11.2144 | 61127 | INTN132 132.00 | T1 | INTN132 | INTN132T1 | 16.5214 | INTN132 132.00 | T1 | INTN132 | INTN132T1 | 16.5214 | 61127 | TMOH132T4
132/11kV T2 & T3 | 32 & 33 | 32.3916 |  | MUAR 11kV | 63127 | T3 | 49.1 | TMOH132 | TMOH132T3 | PERAK | 11.3905 | 61127 | INTN132 132.00 | T2 | INTN132 | INTN132T2 | 15.0354 | INTN132 132.00 | T2 | INTN132 | INTN132T2 | 15.0354 | 61127 | TMOH132T3
132/11kV T1 & T2 | 31 & 32 | 18.9852 |  | BRGS 11 kV | 63155 | T4 | 49.1 | KLBG132 | KLBG132T4 | PERAK | 11.2352 | 61127 | INTN132 132.00 | T3 | INTN132 | INTN132T3 | 25.3708 | INTN132 132.00 | T3 | INTN132 | INTN132T3 | 25.3708 | 61127 | KLBG132T4
IGBK 1 & 2 | 705 & 805 | 130 |  | IGBK & NKST | 63155 | T3 | 49.1 | KLBG132 | KLBG132T3 | PERAK | 11.2807 | 61127 | INTN132 132.00 | T4 | INTN132 | INTN132T4 | 24.5185 | INTN132 132.00 | T4 | INTN132 | INTN132T4 | 24.5185 | 61127 | KLBG132T3
132/33kV T3 & T4 | 3T0 & 4T0 | 41.8364 |  | BBTG 33kV | 63142 | T2 | 49.1 | NKAN132 | NKAN132T2 | PERAK | 14.8076 | 61107 | JENG132 132.00 | T1 | JENG132 | JENG132T1 | 14.4773 | JENG132 132.00 | T1 | JENG132 | JENG132T1 | 14.4773 | 61107 | NKAN132T2
132/11kV T1 & T2 | 31 & 32 | 28.0406 |  | BIMK 11kV | 63142 | T1 | 49.1 | NKAN132 | NKAN132T1 | PERAK | 14.7455 | 61107 | JENG132 132.00 | T2 | JENG132 | JENG132T2 | 13.914 | JENG132 132.00 | T2 | JENG132 | JENG132T2 | 13.914 | 61107 | NKAN132T1
132/33kV T3 & T4 | 3T0 & 4T0 | 98.0819 |  | BIMK 33kV | 63134 | T2 | 49.1 | TASK132 | TASK132T2 | PERAK | 4.7219 | 61141 | KERC132 132.00 | T1 | KERC132 | KERC132T1 | 0 | KERC132 132.00 | T1 | KERC132 | KERC132T1 | 0 | 61141 | TASK132T2
132/11kV T1 & T2 | 31 & 32 | 23.208 |  | BNTG 11kV | 63134 | T1 | 49.1 | TASK132 | TASK132T1 | PERAK | 4.8461 | 61141 | KERC132 132.00 | T2 | KERC132 | KERC132T2 | 0 | KERC132 132.00 | T2 | KERC132 | KERC132T2 | 0 | 61141 | TASK132T1
132/33 kV T1 & T2 | 1T0 & 2T0 |  |  | BWTN 33kV | 88162 | T5 | 49.1 | SPKC132 | SPKC132T5 | WPKL | 55.7688 | 61122 | KKTL132 132.00 | T1 | KKTL132 | KKTL132T1 | 2.9998 | KKTL132 132.00 | T1 | KKTL132 | KKTL132T1 | 2.9998 | 61122 | SPKC132T5
132/11kV T5 | 35 |  |  | BWTN 11kV | 88162 | T4 | 49.1 | SPKC132 | SPKC132T4 | WPKL | 49.4036 | 61122 | KKTL132 132.00 | T2 | KKTL132 | KKTL132T2 | 6.8405 | KKTL132 132.00 | T2 | KKTL132 | KKTL132T2 | 6.8405 | 61122 | SPKC132T4
132/33kV T3 & T4 | 3T0 & 4T0 | 61.6121 |  | PRGS 33 kV | 88162 | T3 | 49.1 | SPKC132 | SPKC132T3 | WPKL | 49.6522 | 61122 | KKTL132 132.00 | T3 | KKTL132 | KKTL132T3 | 20.566 | KKTL132 132.00 | T3 | KKTL132 | KKTL132T3 | 20.566 | 61122 | SPKC132T3
132/33kV T1 & T2 | 1T0 & 2T0 | 85.1885 |  | SRDR 33kV | 51023 | T2 | 49.1 | NUNI132 | NUNI132T2 | SELANGOR | 13.096 | 61122 | KKTL132 132.00 | T4 | KKTL132 | KKTL132T4 | 20.7876 | KKTL132 132.00 | T4 | KKTL132 | KKTL132T4 | 20.7876 | 61122 | NUNI132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 75.8672 |  | AMPG T3&T4 | 51023 | T1 | 49.1 | NUNI132 | NUNI132T1 | SELANGOR | 12.719 | 61113 | KLIM132 132.00 | T1 | KLIM132 | KLIM132T1 | 34.6395 | KLIM132 132.00 | T1 | KLIM132 | KLIM132T1 | 34.6395 | 61113 | NUNI132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 65.0735 |  | AHTM 33kV | 97186 | T2 | 49.1 | TBRU132 | TBRU132T2 | JOHOR | 0 | 61113 | KLIM132 132.00 | T2 | KLIM132 | KLIM132T2 | 34.8683 | KLIM132 132.00 | T2 | KLIM132 | KLIM132T2 | 34.8683 | 61113 | TBRU132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 85.6804 |  | BJLL 33kV | 97186 | T1 | 49.1 | TBRU132 | TBRU132T1 | JOHOR | 23.2293 | 61135 | KSSM132 132.00 | T1 | KSSM132 | KSSM132T1 | 5.3318 | KSSM132 132.00 | T1 | KSSM132 | KSSM132T1 | 5.3318 | 61135 | TBRU132T1
132/33kV T3 & T4 | 3T0 & 4T0 | 52.1303 |  | BLKG 33 kV | 74145 | T2 | 49.1 | KRYG132 | KRYG132T2 | PAHANG | 0 | 61135 | KSSM132 132.00 | T2 | KSSM132 | KSSM132T2 | 5.3515 | KSSM132 132.00 | T2 | KSSM132 | KSSM132T2 | 5.3515 | 61135 | KRYG132T2
132/33kV T1 & T3 & T5 | 1T0 & 3T0 & 5T0 | 82.5745 |  | KBRU 33kV | 74145 | T1 | 49.1 | KRYG132 | KRYG132T1 | PAHANG | 31.6769 | 61135 | KSSM132 132.00 | T3 | KSSM132 | KSSM132T3 | 12.456 | KSSM132 132.00 | T3 | KSSM132 | KSSM132T3 | 12.456 | 61135 | KRYG132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 65.7207 |  | PJST 33 kV | 96141 | F2 | 49.1 | SHEL132 | SHEL132F2 | NS | 19.1541 | 61135 | KSSM132 132.00 | T4 | KSSM132 | KSSM132T4 | 12.5658 | KSSM132 132.00 | T4 | KSSM132 | KSSM132T4 | 12.5658 | 61135 | SHEL132F2
132/33kV T1 & T2 | 1T0 & 2T0 | 111.1269 |  | PGTC 33kV | 96141 | F1 | 49.1 | SHEL132 | SHEL132F1 | NS | 18.1541 | 561111 | KSTR132R 132.00 | T8 | KSTR132 | KSTR132T8 | 26.6486 | KSTR132R 132.00 | T8 | KSTR132 | KSTR132T8 | 26.6486 | 561111 | SHEL132F1
132/22kV T1 & T2 | 1T0 & 2T0 | 37.2708 |  | PGIE 22kV | 51072 | T2 | 49.1 | HCOM132 | HCOM132T2 | SELANGOR | 34.0078 | 161111 | KSTR_T 132.00 | T7 | KSTR_T | KSTR_T T7 | 36.2766 | KSTR_T 132.00 | T7 | KSTR_T | KSTR_T T7 | 36.2766 | 161111 | HCOM132T2
132/22kV T3 | 3T0 | 15.0562 |  | PGIE 22kV | 51072 | T1 | 49.1 | HCOM132 | HCOM132T1 | SELANGOR | 38.7888 | 61119 | MGON132 132.00 | T1 | MGON132 | MGON132T1 | 8.2591 | MGON132 132.00 | T1 | MGON132 | MGON132T1 | 8.2591 | 61119 | HCOM132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 83.0514 |  | PCHJ 33kV | 51017 | T5 | 49.1 | SHAE132 | SHAE132T5 | SELANGOR | 32.8543 | 61119 | MGON132 132.00 | T2 | MGON132 | MGON132T2 | 8.2529 | MGON132 132.00 | T2 | MGON132 | MGON132T2 | 8.2529 | 61119 | SHAE132T5
132/33kV T1 & T2 | 1T0 & 2T0 | 62.5762 |  | NSDA 33 kV | 51017 | T4 | 49.1 | SHAE132 | SHAE132T4 | SELANGOR | 24.0681 | 61119 | MGON132 132.00 | T3 | MGON132 | MGON132T3 | 49.2349 | MGON132 132.00 | T3 | MGON132 | MGON132T3 | 49.2349 | 61119 | SHAE132T4
132/33kV T1 & T2 | 1T0 & 2T0 | 67.9905 |  | SDAM 33kV | 51017 | T3 | 49.1 | SHAE132 | SHAE132T3 | SELANGOR | 23.7854 | 61119 | MGON132 132.00 | T4 | MGON132 | MGON132T4 | 45.9689 | MGON132 132.00 | T4 | MGON132 | MGON132T4 | 45.9689 | 61119 | SHAE132T3
132/33kV T1 & T2 | 1T0 & 2T0 | 68.1678 |  | NSPK 33 kV | 51007 | T2 | 49.1 | SHAS132 | SHAS132T2 | SELANGOR | 39.0476 | 61132 | PAUH132 132.00 | T1 | PAUH132 | PAUH132T1 | 18.8088 | PAUH132 132.00 | T1 | PAUH132 | PAUH132T1 | 18.8088 | 61132 | SHAS132T2
132/33kV T1 & T2 | 1T0&2T0 | 51.941 |  | SRDN 33kV | 51007 | T1 | 49.1 | SHAS132 | SHAS132T1 | SELANGOR | 38.9275 | 61132 | PAUH132 132.00 | T2 | PAUH132 | PAUH132T2 | 18.9869 | PAUH132 132.00 | T2 | PAUH132 | PAUH132T2 | 18.9869 | 61132 | SHAS132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 64.8369 |  | SDYN 33kV | 75129 | T4 | 49.1 | PCOR132 | PCOR132T4 | KELANTAN | 29.6256 | 61132 | PAUH132 132.00 | T3 | PAUH132 | PAUH132T3 | 10.7723 | PAUH132 132.00 | T3 | PAUH132 | PAUH132T3 | 10.7723 | 61132 | PCOR132T4
132/11kV T1 & T2 | 31 & 32 | 17.6596 |  | LKUT 11kV | 75129 | T3 | 49.1 | PCOR132 | PCOR132T3 | KELANTAN | 32.9402 | 61132 | PAUH132 132.00 | T4 | PAUH132 | PAUH132T4 | 10.8261 | PAUH132 132.00 | T4 | PAUH132 | PAUH132T4 | 10.8261 | 61132 | PCOR132T3
132/11kV T1 & T2 & T3 | 31 & 32 & 33 | 25.8429 |  | TGLN 11kV | 75129 | T2 | 49.1 | PCOR132 | PCOR132T2 | KELANTAN | 38.9658 | 61132 | PAUH132 132.00 | T5 | PAUH132 | PAUH132T5 | 11.9787 | PAUH132 132.00 | T5 | PAUH132 | PAUH132T5 | 11.9787 | 61132 | PCOR132T2
132/11kV T1 & T2 | 31 & 32 | 25.7531 |  | KSTR 11kV | 97110 | T2 | 49.1 | JTGH132 | JTGH132T2 | JOHOR | 12.2458 | 61106 | SPID132 132.00 | T1 | SPID132 | SPID132T1 | 9.7471 | SPID132 132.00 | T1 | SPID132 | SPID132T1 | 9.7471 | 61106 | JTGH132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 71.7948 |  | KCPK 33kV | 97110 | T1 | 49.1 | JTGH132 | JTGH132T1 | JOHOR | 12.193 | 61106 | SPID132 132.00 | T2 | SPID132 | SPID132T2 | 10.0816 | SPID132 132.00 | T2 | SPID132 | SPID132T2 | 10.0816 | 61106 | JTGH132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 74.945 |  | NRWG 33 kV | 62112 | T2 | 49.1 | SJAY132 | SJAY132T2 | P PINANG | 42.9918 | 61106 | SPID132 132.00 | T3 | SPID132 | SPID132T3 | 43.6566 | SPID132 132.00 | T3 | SPID132 | SPID132T3 | 43.6566 | 61106 | SJAY132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 69.4631 |  | BKPR 33kV | 62112 | T1 | 49.1 | SJAY132 | SJAY132T1 | P PINANG | 42.5776 | 61106 | SPID132 132.00 | T4 | SPID132 | SPID132T4 | 43.9507 | SPID132 132.00 | T4 | SPID132 | SPID132T4 | 43.9507 | 61106 | SJAY132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 60.1524 |  | TMSY 33 kV | 61127 | T4 | 49.1 | INTN132 | INTN132T4 | KEDAH | 24.5185 | 61112 | TKBU132 132.00 | T1 | TKBU132 | TKBU132T1 | 31.6376 | TKBU132 132.00 | T1 | TKBU132 | TKBU132T1 | 31.6376 | 61112 | INTN132T4
MTNH 1 & 2 | 105 & 205 | 49 |  | TKMG, PPJG, MTNH | 61127 | T3 | 49.1 | INTN132 | INTN132T3 | KEDAH | 25.3708 | 61112 | TKBU132 132.00 | T2 | TKBU132 | TKBU132T2 | 31.707 | TKBU132 132.00 | T2 | TKBU132 | TKBU132T2 | 31.707 | 61112 | INTN132T3
TKMG 1 & 2 | 105 & 205 |  |  |  | 61127 | T2 | 49.1 | INTN132 | INTN132T2 | KEDAH | 15.0354 | 62105 | ATJN132 132.00 | T1 | ATJN132 | ATJN132T1 | 5.3577 | ATJN132 132.00 | T1 | ATJN132 | ATJN132T1 | 5.3577 | 62105 | INTN132T2
TJID 1 & 2 | 105 & 205 | 140 |  | TJID, TTJF, SSUN & STRA | 61127 | T1 | 49.1 | INTN132 | INTN132T1 | KEDAH | 16.5214 | 62105 | ATJN132 132.00 | T2 | ATJN132 | ATJN132T2 | 9.6001 | ATJN132 132.00 | T2 | ATJN132 | ATJN132T2 | 9.6001 | 62105 | INTN132T1
Satria & TTJF | 505 & 605 |  |  |  | 96177 | T2 | 49.1 | MPSS132 | MPSS132T2 | MELAKA | 6.0121 | 62105 | ATJN132 132.00 | T3 | ATJN132 | ATJN132T3 | 22.4579 | ATJN132 132.00 | T3 | ATJN132 | ATJN132T3 | 22.4579 | 62105 | MPSS132T2
BNTG & RBDR | 205 & 405 | 133 |  | BNTA, KLIP, JNKA, JTUT, RBDR | 96177 | T1 | 49.1 | MPSS132 | MPSS132T1 | MELAKA | 2.9429 | 62105 | ATJN132 132.00 | T4 | ATJN132 | ATJN132T4 | 23.0864 | ATJN132 132.00 | T4 | ATJN132 | ATJN132T4 | 23.0864 | 62105 | MPSS132T1
JNKA & JTUT | 205 & 705 |  |  |  | 75127 | T2 | 49 | TJUG132 | TJUG132T2 | KELANTAN | 30.4043 | 62131 | BBRU132 132.00 | T1 | BBRU132 | BBRU132T1 | 48.453 | BBRU132 132.00 | T1 | BBRU132 | BBRU132T1 | 48.453 | 62131 | TJUG132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 56.7503 |  | ATJN 33 kV | 75127 | T1 | 49 | TJUG132 | TJUG132T1 | KELANTAN | 26.6216 | 62131 | BBRU132 132.00 | T2 | BBRU132 | BBRU132T2 | 48.1662 | BBRU132 132.00 | T2 | BBRU132 | BBRU132T2 | 48.1662 | 62131 | TJUG132T1
132/11kV T1 & T2 | 31 & 32 | 9.3912 |  | GRUN 11kV | 97147 | T3 | 49 | MUAR132 | MUAR132T3 | JOHOR | 12.6041 | 62131 | BBRU132 132.00 | T3 | BBRU132 | BBRU132T3 | 5.367 | BBRU132 132.00 | T3 | BBRU132 | BBRU132T3 | 5.367 | 62131 | MUAR132T3
132/33kV T1 & T2 | 1T0 & 2T0 | 22.7999 |  | JENG 33kV | 97147 | T2 | 49 | MUAR132 | MUAR132T2 | JOHOR | 9.4168 | 62131 | BBRU132 132.00 | T4 | BBRU132 | BBRU132T4 | 11.4205 | BBRU132 132.00 | T4 | BBRU132 | BBRU132T4 | 11.4205 | 62131 | MUAR132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 58.1226 |  | LMUT 33kV | 51004 | T2 | 49 | BRGS132 | BRGS132T2 | SELANGOR | 10.8178 | 562131 | BBRU132NEW 132.00 | T2 | BBRU132 | BBRU132T2 | 41.7733 | BBRU132NEW 132.00 | T2 | BBRU132 | BBRU132T2 | 41.7733 | 562131 | BRGS132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 72.3964 |  | LMTM 33kV | 51004 | T1 | 49 | BRGS132 | BRGS132T1 | SELANGOR | 8.0603 | 562131 | BBRU132NEW 132.00 | T4 | BBRU132 | BBRU132T4 | 12.6684 | BBRU132NEW 132.00 | T4 | BBRU132 | BBRU132T4 | 12.6684 | 562131 | BRGS132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 38.9019 |  | MDAM 33kV | 51047 | T2 | 49 | IGBK132 | IGBK132T2 | SELANGOR | 11.6069 | 562131 | BBRU132NEW 132.00 | T8 | BBRU132 | BBRU132T8 | 14.1979 | BBRU132NEW 132.00 | T8 | BBRU132 | BBRU132T8 | 14.1979 | 562131 | IGBK132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 84.9599 |  | BCVS 33kV | 51047 | T1 | 49 | IGBK132 | IGBK132T1 | SELANGOR | 10.7733 | 62120 | BKWS132 132.00 | T1 | BKWS132 | BKWS132T1 | 55.8776 | BKWS132 132.00 | T1 | BKWS132 | BKWS132T1 | 55.8776 | 62120 | IGBK132T1
132/11kV T1 & T2 | 31 & 32 | 17.3238 |  | PRJA 11kV | 51087 | T4 | 49 | BBTG132 | BBTG132T4 | SELANGOR | 19.8681 | 62120 | BKWS132 132.00 | T2 | BKWS132 | BKWS132T2 | 54.3657 | BKWS132 132.00 | T2 | BKWS132 | BKWS132T2 | 54.3657 | 62120 | BBTG132T4
CAAH & BSPT/BKPG | 105 & 205 | 298 |  | LKJG, XNSS, XNYI, TKID, TKAK, JMTH, SGMT, BSPT, BKPG, CAAH, BAHA, NSCI, GMAS, PBSR, KLPH, SPTG, KKWG | 51087 | T3 | 49 | BBTG132 | BBTG132T3 | SELANGOR | 20.0307 | 62120 | BKWS132 132.00 | T5 | BKWS132 | BKWS132T5 | 1.0262 | BKWS132 132.00 | T5 | BKWS132 | BKWS132T5 | 1.0262 | 62120 | BBTG132T3
KPLH 1 & 2 | 705 & 805 |  |  |  | 74128 | T4 | 49 | BIMK132 | BIMK132T4 | PAHANG | 37.6424 | 61117 | BLIN132 132.00 | T1 | BLIN132 | BLIN132T1 | 15.6174 | BLIN132 132.00 | T1 | BLIN132 | BLIN132T1 | 15.6174 | 61117 | BIMK132T4
JSIN & MCOP | 505 & 605 |  |  |  | 74128 | T3 | 49 | BIMK132 | BIMK132T3 | PAHANG | 37.4146 | 61117 | BLIN132 132.00 | T2 | BLIN132 | BLIN132T2 | 14.2102 | BLIN132 132.00 | T2 | BLIN132 | BLIN132T2 | 14.2102 | 61117 | BIMK132T3
132/11kV T1 & T2 | 31 & 32 | 18 |  | UPSR 11kV | 74128 | T2 | 49 | BIMK132 | BIMK132T2 | PAHANG | 11.2828 | 62102 | BLPS132L 132.00 | T3 | BLPS132 | BLPS132T3 | 43.2683 | BLPS132L 132.00 | T3 | BLPS132 | BLPS132T3 | 43.2683 | 62102 | BIMK132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 60 |  | UPSR 33kV | 74128 | T1 | 49 | BIMK132 | BIMK132T1 | PAHANG | 10.0526 | 62102 | BLPS132L 132.00 | T4 | BLPS132 | BLPS132T4 | 46.5798 | BLPS132L 132.00 | T4 | BLPS132 | BLPS132T4 | 46.5798 | 62102 | BIMK132T1
132/11kV T1 & T2 | 31 & 32 | 30 |  | MCOP 11kV | 74118 | T2 | 49 | BNTG132 | BNTG132T2 | PAHANG | 11.3387 | 62104 | BLPS132R 132.00 | T1 | BLPS132 | BLPS132T1 | 36.0571 | BLPS132R 132.00 | T1 | BLPS132 | BLPS132T1 | 36.0571 | 62104 | BNTG132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 61 |  | MCOP 33kV | 74118 | T1 | 49 | BNTG132 | BNTG132T1 | PAHANG | 8.081 | 62104 | BLPS132R 132.00 | T2 | BLPS132 | BLPS132T2 | 35.3115 | BLPS132R 132.00 | T2 | BLPS132 | BLPS132T2 | 35.3115 | 62104 | BNTG132T1
132/11kV T1 & T2 | 31 & 32 | 22.8675 |  | NLAI 11kV | 62133 | T2 | 49 | BWTN132 | BWTN132T2 | P PINANG | 39.9982 | 62106 | BMJM132 132.00 | T1 | BMJM132 | BMJM132T1 | 9.5618 | BMJM132 132.00 | T1 | BMJM132 | BMJM132T1 | 9.5618 | 62106 | BWTN132T2
132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 71.3972 |  | BTGA 33kV | 62133 | T1 | 49 | BWTN132 | BWTN132T1 | P PINANG | 38.7007 | 62106 | BMJM132 132.00 | T2 | BMJM132 | BMJM132T2 | 12.9313 | BMJM132 132.00 | T2 | BMJM132 | BMJM132T2 | 12.9313 | 62106 | BWTN132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 66.6988 |  | BBDG 33kV | 62133 | T5 | 49 | BWTN132 | BWTN132T5 | P PINANG | 0 | 62106 | BMJM132 132.00 | T3 | BMJM132 | BMJM132T3 | 21.293 | BMJM132 132.00 | T3 | BMJM132 | BMJM132T3 | 21.293 | 62106 | BWTN132T5
132/11kV T1 & T2 | 31 & 32 | 31.7609 |  | RSID 11kV | 562137 | T4 | 49 | PRGS132 | PRGS132T4 | P PINANG | 21.0061 | 62106 | BMJM132 132.00 | T4 | BMJM132 | BMJM132T4 | 21.2712 | BMJM132 132.00 | T4 | BMJM132 | BMJM132T4 | 21.2712 | 62106 | PRGS132T4
132/11kV T1 & T2 | 31 & 32 | 21.3927 |  | GRSK 11kV | 562137 | T3 | 49 | PRGS132 | PRGS132T3 | P PINANG | 21.0455 | 62110 | BMTR132 132.00 | T1 | BMTR132 | BMTR132T1 | 62.7419 | BMTR132 132.00 | T1 | BMTR132 | BMTR132T1 | 62.7419 | 62110 | PRGS132T3
132/22kV T1 & T2 | 1T0 & 2T0 | 35.0813 |  | KPTR 22kV | 51130 | T2 | 49 | SRDR132 | SRDR132T2 | WPKL | 27.9781 | 62110 | BMTR132 132.00 | T2 | BMTR132 | BMTR132T2 | 57.494 | BMTR132 132.00 | T2 | BMTR132 | BMTR132T2 | 57.494 | 62110 | SRDR132T2
132/22kV T7 & T8 | 37 & 38 | 1.4469 |  | SDAI 22kV | 51130 | T1 | 49 | SRDR132 | SRDR132T1 | WPKL | 27.8539 | 62108 | BMYK132 132.00 | T1 | BMYK132 | BMYK132T1 | 11.9517 | BMYK132 132.00 | T1 | BMYK132 | BMYK132T1 | 11.9517 | 62108 | SRDR132T1
132/22kV T1 & T2 | 1T0 & 2T0 | 33.3325 |  | LKIN 22kV | 88120 | T4 | 49 | AMPG132 | AMPG132T4 | WPKL | 42.4761 | 62108 | BMYK132 132.00 | T2 | BMYK132 | BMYK132T2 | 14.6306 | BMYK132 132.00 | T2 | BMYK132 | BMYK132T2 | 14.6306 | 62108 | AMPG132T4
SONG | 605 | 90 |  | SONG, MTKB, TMID, MNID | 88120 | T3 | 49 | AMPG132 | AMPG132T3 | WPKL | 42.5704 | 62108 | BMYK132 132.00 | T3 | BMYK132 | BMYK132T3 | 49.2069 | BMYK132 132.00 | T3 | BMYK132 | BMYK132T3 | 49.2069 | 62108 | AMPG132T3
TMID | 205 |  |  |  | 51028 | T2 | 49 | AHTM132 | AHTM132T2 | SELANGOR | 44.3266 | 62108 | BMYK132 132.00 | T4 | BMYK132 | BMYK132T4 | 48.2977 | BMYK132 132.00 | T4 | BMYK132 | BMYK132T4 | 48.2977 | 62108 | AHTM132T2
132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 61.1334 |  | GLGR 33kV | 51028 | T1 | 49 | AHTM132 | AHTM132T1 | SELANGOR | 43.4909 | 62101 | BTBN132 132.00 | T1 | BTBN132 | BTBN132T1 | 40.3296 | BTBN132 132.00 | T1 | BTBN132 | BTBN132T1 | 40.3296 | 62101 | AHTM132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 105.8642 |  | BMTR 33kV | 88177 | T2 | 49 | BJLL132 | BJLL132T2 | SELANGOR | 39.4804 | 62101 | BTBN132 132.00 | T2 | BTBN132 | BTBN132T2 | 40.7624 | BTBN132 132.00 | T2 | BTBN132 | BTBN132T2 | 40.7624 | 62101 | BJLL132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 52.4377 |  | BTWS 33kV | 88177 | T1 | 49 | BJLL132 | BJLL132T1 | SELANGOR | 39.4245 | 462114 | BTGH132NEW 132.00 | T1 | BTGH132 | BTGH132T1 | 49.9835 | BTGH132NEW 132.00 | T1 | BTGH132 | BTGH132T1 | 49.9835 | 462114 | BJLL132T1
132/33kV T3 & T4 | 3T0 & 4T0 | 14.2995 |  | KGAR 33kV | 51062 | T4 | 49 | BLKG132 | BLKG132T4 | SELANGOR | 41.9139 | 462114 | BTGH132NEW 132.00 | T2 | BTGH132 | BTGH132T2 | 47.0033 | BTGH132NEW 132.00 | T2 | BTGH132 | BTGH132T2 | 47.0033 | 462114 | BLKG132T4
132/33kV T3 & T4 | 3T0 & 4T0 | 69.0504 |  | SHAW 33kV | 51062 | T3 | 49 | BLKG132 | BLKG132T3 | SELANGOR | 42.6936 | 62133 | BWTN132 132.00 | T1 | BWTN132 | BWTN132T1 | 38.7007 | BWTN132 132.00 | T1 | BWTN132 | BWTN132T1 | 38.7007 | 62133 | BLKG132T3
132/11kV T1 & T2 | 31 & 32 | 15.0282 |  | SHAW 11kV | 75112 | T5 | 48.9 | KBRU132 | KBRU132T5 | KELANTAN | 24.9814 | 62133 | BWTN132 132.00 | T2 | BWTN132 | BWTN132T2 | 39.9982 | BWTN132 132.00 | T2 | BWTN132 | BWTN132T2 | 39.9982 | 62133 | KBRU132T5
132/33kV T3 & T4 | 3T0 & 4T0 | 98.751 |  | TPGR 33kV | 75112 | T3 | 48.9 | KBRU132 | KBRU132T3 | KELANTAN | 24.9265 | 62133 | BWTN132 132.00 | T5 | BWTN132 | BWTN132T5 | 0 | BWTN132 132.00 | T5 | BWTN132 | BWTN132T5 | 0 | 62133 | KBRU132T3
132/11kV T1, T2 & T3 | 31, 32 & 33 | 4.0549 |  | SHAN 11kV | 75112 | T1 | 48.9 | KBRU132 | KBRU132T1 | KELANTAN | 25.5758 | 62109 | DKMT132 132.00 | T1 | DKMT132 | DKMT132T1 | 8.9374 | DKMT132 132.00 | T1 | DKMT132 | DKMT132T1 | 8.9374 | 62109 | KBRU132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 77.1695 |  | SHLB 33kV | 51082 | T2 | 48.9 | PJST132 | PJST132T2 | SELANGOR | 26.5481 | 62109 | DKMT132 132.00 | T2 | DKMT132 | DKMT132T2 | 8.9964 | DKMT132 132.00 | T2 | DKMT132 | DKMT132T2 | 8.9964 | 62109 | PJST132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 81.8867 |  | BBTC 33kV | 51082 | T1 | 48.9 | PJST132 | PJST132T1 | SELANGOR | 26.5398 | 61163 | EVEM132 132.00 | T1 | EVEM132 | EVEM132T1 | 1.1542 | EVEM132 132.00 | T1 | EVEM132 | EVEM132T1 | 1.1542 | 61163 | PJST132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 45.0985 |  | BDNG 33kV | 97167 | T2 | 48.9 | PGTC132 | PGTC132T2 | JOHOR | 47.6754 | 61163 | EVEM132 132.00 | T2 | EVEM132 | EVEM132T2 | 3.5837 | EVEM132 132.00 | T2 | EVEM132 | EVEM132T2 | 3.5837 | 61163 | PGTC132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 71.6655 |  | KULN 33kV | 97167 | T1 | 48.9 | PGTC132 | PGTC132T1 | JOHOR | 47.8349 | 62103 | FLIM132 132.00 | T1 | FLIM132 | FLIM132T1 | 11.464 | FLIM132 132.00 | T1 | FLIM132 | FLIM132T1 | 11.464 | 62103 | PGTC132T1
132/11kV T1 & T2 | 31 & 32 | 9.9042 |  | DGUN 11kV | 97123 | T2 | 48.9 | PGIE132 | PGIE132T2 | JOHOR | 13.8715 | 62103 | FLIM132 132.00 | T2 | FLIM132 | FLIM132T2 | 5.8651 | FLIM132 132.00 | T2 | FLIM132 | FLIM132T2 | 5.8651 | 62103 | PGIE132T2
132/11kV T1 & T2 | 31 & 32 | 18.4411 |  | CHRG 11kV | 97123 | T1 | 48.9 | PGIE132 | PGIE132T1 | JOHOR | 13.8622 | 62103 | FLIM132 132.00 | T3 | FLIM132 | FLIM132T3 | 26.7438 | FLIM132 132.00 | T3 | FLIM132 | FLIM132T3 | 26.7438 | 62103 | PGIE132T1
132/11kV T1 & T2 | 31 & 32 | 20.3434 |  | KLUG 11kV | 97123 | T3 | 48.9 | PGIE132 | PGIE132T3 | JOHOR | 12.4343 | 62103 | FLIM132 132.00 | T4 | FLIM132 | FLIM132T4 | 23.2676 | FLIM132 132.00 | T4 | FLIM132 | FLIM132T4 | 23.2676 | 62103 | PGIE132T3
132/22kV T1 & T2 | 1T0 & 2T0 | 34.6464 |  | MAJD 22kV | 88174 | T2 | 48.9 | PCHJ132 | PCHJ132T2 | SELANGOR | 30.6476 | 62118 | GLGR132 132.00 | T1 | GLGR132 | GLGR132T1 | 19.1961 | GLGR132 132.00 | T1 | GLGR132 | GLGR132T1 | 19.1961 | 62118 | PCHJ132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 17.7645 |  | DGID 33kV | 88174 | T1 | 48.9 | PCHJ132 | PCHJ132T1 | SELANGOR | 30.6073 | 62118 | GLGR132 132.00 | T2 | GLGR132 | GLGR132T2 | 21.3737 | GLGR132 132.00 | T2 | GLGR132 | GLGR132T2 | 21.3737 | 62118 | PCHJ132T1
132/11kV T1 & T2 | 31 & 32 | 16.51 |  | CKAI 11kV | 51025 | T2 | 48.9 | NSDA132 | NSDA132T2 | SELANGOR | 31.0919 | 62118 | GLGR132 132.00 | T3 | GLGR132 | GLGR132T3 | 21.4069 | GLGR132 132.00 | T3 | GLGR132 | GLGR132T3 | 21.4069 | 62118 | NSDA132T2
132/11kV T3 & T4 | 35 & 36 | 20.2035 |  | PAUH 11kV | 51025 | T1 | 48.9 | NSDA132 | NSDA132T1 | SELANGOR | 31.0536 | 62221 | ITLM275 275.00 | F1 | ITLM275 | ITLM275F1 | 0 | ITLM275 275.00 | F1 | ITLM275 | ITLM275F1 | 0 | 62221 | NSDA132T1
132/11kV T1 & T2 | 31 & 32 | 40.4944 |  | BMYK 11kV | 88173 | T2 | 48.9 | SDAM132 | SDAM132T2 | WPKL | 27.6488 | 62221 | ITLM275 275.00 | F2 | ITLM275 | ITLM275F2 | 0 | ITLM275 275.00 | F2 | ITLM275 | ITLM275F2 | 0 | 62221 | SDAM132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 99.6068 |  | BMYK 33kV | 88173 | T1 | 48.9 | SDAM132 | SDAM132T1 | WPKL | 27.8943 | 62111 | NTBL132 132.00 | T1 | NTBL132 | NTBL132T1 | 11.9238 | NTBL132 132.00 | T1 | NTBL132 | NTBL132T1 | 11.9238 | 62111 | SDAM132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 70.4984 |  | PRID 33kV | 51091 | T2 | 48.9 | NSPK132 | NSPK132T2 | SELANGOR | 25.7756 | 62111 | NTBL132 132.00 | T2 | NTBL132 | NTBL132T2 | 14.8252 | NTBL132 132.00 | T2 | NTBL132 | NTBL132T2 | 14.8252 | 62111 | NSPK132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 99.1207 |  |  | 51091 | T1 | 48.9 | NSPK132 | NSPK132T1 | SELANGOR | 26.3079 | 62137 | PRGS132 132.00 | T1 | PRGS132 | PRGS132T1 | 12.5585 | PRGS132 132.00 | T1 | PRGS132 | PRGS132T1 | 12.5585 | 62137 | NSPK132T1
132/33kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 96.6747 |  | PCHP 33kV | 51050 | T2 | 48.9 | SRDN132 | SRDN132T2 | WPKL | 24.2006 | 62137 | PRGS132 132.00 | T2 | PRGS132 | PRGS132T2 | 7.584 | PRGS132 132.00 | T2 | PRGS132 | PRGS132T2 | 7.584 | 62137 | SRDN132T2
132/33kV T3 & T4 | 3T0 & 4T0 | 127.7547 |  | CBPS 33kV | 51050 | T1 | 48.9 | SRDN132 | SRDN132T1 | WPKL | 24.2483 | 562137 | PRGS132R 132.00 | T3 | PRGS132 | PRGS132T3 | 21.0455 | PRGS132R 132.00 | T3 | PRGS132 | PRGS132T3 | 21.0455 | 562137 | SRDN132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 90.9176 |  | SHAB 33kV | 96150 | T2 | 48.9 | SDYN132 | SDYN132T2 | NS | 45.0318 | 562137 | PRGS132R 132.00 | T4 | PRGS132 | PRGS132T4 | 21.0061 | PRGS132R 132.00 | T4 | PRGS132 | PRGS132T4 | 21.0061 | 562137 | SDYN132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 81.4331 |  | SGBT 33kV | 96150 | T1 | 48.9 | SDYN132 | SDYN132T1 | NS | 44.7532 | 62155 | PRID132 132.00 | T1 | PRID132 | PRID132T1 | 23.6135 | PRID132 132.00 | T1 | PRID132 | PRID132T1 | 23.6135 | 62155 | SDYN132T1
275/33kV T1 & T2 | 1T0 & 2T1 | 16.6814 |  | JELI 33kV | 96134 | T2 | 48.9 | LKUT132 | LKUT132T2 | NS | 10 | 62155 | PRID132 132.00 | T2 | PRID132 | PRID132T2 | 23.4313 | PRID132 132.00 | T2 | PRID132 | PRID132T2 | 23.4313 | 62155 | LKUT132T2
Pasir Putih 1 & 2 | 305 & 405 | 83 |  | PPTH & SJTH | 96134 | T1 | 48.9 | LKUT132 | LKUT132T1 | NS | 12.0335 | 62155 | PRID132 132.00 | T3 | PRID132 | PRID132T3 | 36.8203 | PRID132 132.00 | T3 | PRID132 | PRID132T3 | 36.8203 | 62155 | LKUT132T1
Pasir Putih 1 & 2 | 505 & 605 |  |  |  | 74106 | T2 | 48.9 | TGLN132 | TGLN132T2 | PAHANG | 5.2148 | 62155 | PRID132 132.00 | T4 | PRID132 | PRID132T4 | 36.9093 | PRID132 132.00 | T4 | PRID132 | PRID132T4 | 36.9093 | 62155 | TGLN132T2
CHNG & ZRNA | 305 & 805 | 268 |  | ZRNA, SPWR, CHNG, BMKA, MMKA, BVTA, MFDR, TGBU, PPSR, HLNM, BRBI | 74106 | T1 | 48.9 | TGLN132 | TGLN132T1 | PAHANG | 5.9562 | 62128 | SARA132 132.00 | T1 | SARA132 | SARA132T1 | 35.6077 | SARA132 132.00 | T1 | SARA132 | SARA132T1 | 35.6077 | 62128 | TGLN132T1
BVTA 1 & 2 | 705 & 805 |  |  |  | 74106 | T3 | 48.9 | TGLN132 | TGLN132T3 | PAHANG | 11.2642 | 62128 | SARA132 132.00 | T2 | SARA132 | SARA132T2 | 35.7174 | SARA132 132.00 | T2 | SARA132 | SARA132T2 | 35.7174 | 62128 | TGLN132T3
BRBI 1 & 2 | 705 & 805 |  |  |  | #N/A | T2 | 48.8 | KSTR132 | KSTR132T2 | #N/A | #N/A | 62112 | SJAY132 132.00 | T1 | SJAY132 | SJAY132T1 | 42.5776 | SJAY132 132.00 | T1 | SJAY132 | SJAY132T1 | 42.5776 | 62112 | KSTR132T2
TGBU 1 & 2 | 905 & 1005 |  |  |  | #N/A | T1 | 48.8 | KSTR132 | KSTR132T1 | #N/A | #N/A | 62112 | SJAY132 132.00 | T2 | SJAY132 | SJAY132T2 | 42.9918 | SJAY132 132.00 | T2 | SJAY132 | SJAY132T2 | 42.9918 | 62112 | KSTR132T1
KBRG & CHRG/KTGU | 305 & 205 | 153 |  | GBDK, KBRG, KTGU & BRKT | 51031 | T2 | 48.8 | KCPK132 | KCPK132T2 | SELANGOR | 31.0246 | 62107 | SKCL132 132.00 | T1 | SKCL132 | SKCL132T1 | 11.552 | SKCL132 132.00 | T1 | SKCL132 | SKCL132T1 | 11.552 | 62107 | KCPK132T2
KBRG/KTGU & KNYT/KTGU | 205 & 305 |  |  |  | 51031 | T1 | 48.8 | KCPK132 | KCPK132T1 | SELANGOR | 31.1292 | 62107 | SKCL132 132.00 | T2 | SKCL132 | SKCL132T2 | 9.2791 | SKCL132 132.00 | T2 | SKCL132 | SKCL132T2 | 9.2791 | 62107 | KCPK132T1
SNAI & SLNG | 205 & 505 | 232 |  | SLNG, SNAI, KLAI & UTMJ | 51200 | T2 | 48.8 | NRWG132 | NRWG132T2 | SELANGOR | 37.5762 | 62107 | SKCL132 132.00 | T3 | SKCL132 | SKCL132T3 | 22.3989 | SKCL132 132.00 | T3 | SKCL132 | SKCL132T3 | 22.3989 | 62107 | NRWG132T2
SNAI & SLNG | 305 & 405 |  |  |  | 51200 | T1 | 48.8 | NRWG132 | NRWG132T1 | SELANGOR | 37.6476 | 62107 | SKCL132 132.00 | T4 | SKCL132 | SKCL132T4 | 22.9208 | SKCL132 132.00 | T4 | SKCL132 | SKCL132T4 | 22.9208 | 62107 | NRWG132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 14.7682 |  | BTAI 33kV | 51045 | T4 | 48.8 | BKPR132 | BKPR132T4 | SELANGOR | 38.7432 | 62124 | SPAE132 132.00 | T1 | SPAE132 | SPAE132T1 | 36.4433 | SPAE132 132.00 | T1 | SPAE132 | SPAE132T1 | 36.4433 | 62124 | BKPR132T4
132/33kV T1 & T2 | 1T0 & 2T0 | 61.6353 |  | KULE 33kV | 51045 | T3 | 48.8 | BKPR132 | BKPR132T3 | SELANGOR | 38.7349 | 62124 | SPAE132 132.00 | T2 | SPAE132 | SPAE132T2 | 36.0654 | SPAE132 132.00 | T2 | SPAE132 | SPAE132T2 | 36.0654 | 62124 | BKPR132T3
132/33kV T1 & T2 | 1T0 & 2T0 | 68.7869 |  | KLPV 33kV | 51084 | T2 | 48.8 | TMSY132 | TMSY132T2 | SELANGOR | 15.4766 | 62117 | SPG4132 132.00 | T1 | SPG4132 | SPG4132T1 | 0 | SPG4132 132.00 | T1 | SPG4132 | SPG4132T1 | 0 | 62117 | TMSY132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 60.3016 |  | TKBU 33kV | 51084 | T1 | 48.8 | TMSY132 | TMSY132T1 | SELANGOR | 15.5138 | 562117 | SPG4132R 132.00 | T2 | SPG4132 | SPG4132T2 | 0 | SPG4132R 132.00 | T2 | SPG4132 | SPG4132T2 | 0 | 562117 | TMSY132T1
132/22kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 35.9347 |  | TPOI 22kV | 96144 | T2 | 48.8 | TKMG132 | TKMG132T2 | NS | 6.827 | 62135 | SPNG132 132.00 | T1 | SPNG132 | SPNG132T1 | 27.4583 | SPNG132 132.00 | T1 | SPNG132 | SPNG132T1 | 27.4583 | 62135 | TKMG132T2
BPHT 1 & 2 | 305 & 405 | 41 |  | BPHT, TPCH | 96144 | T1 | 48.8 | TKMG132 | TKMG132T1 | NS | 6.8529 | 62135 | SPNG132 132.00 | T2 | SPNG132 | SPNG132T2 | 25.9372 | SPNG132 132.00 | T2 | SPNG132 | SPNG132T2 | 25.9372 | 62135 | TKMG132T1
BPHT & TPCH | 105 & 205 |  |  |  | 96147 | T2 | 48.8 | PPJG132 | PPJG132T2 | MELAKA | 10.589 | 62125 | TGLR132 132.00 | T1 | TGLR132 | TGLR132T1 | 20.4977 | TGLR132 132.00 | T1 | TGLR132 | TGLR132T1 | 20.4977 | 62125 | PPJG132T2
132/11kV T1 & T2 | 31 & 32 | - |  | YGPG 11kV | 96147 | T1 | 48.8 | PPJG132 | PPJG132T1 | MELAKA | 0 | 62125 | TGLR132 132.00 | T2 | TGLR132 | TGLR132T2 | 20.6364 | TGLR132 132.00 | T2 | TGLR132 | TGLR132T2 | 20.6364 | 62125 | PPJG132T1
132/33kV T3 & T4 | 3T0 & 4T0 | 100.9312 |  | MERU 33 kV | 96173 | T6 | 48.8 | MTNH132 | MTNH132T6 | MELAKA | 11.4733 | 62127 | TGTK132 132.00 | T1 | TGTK132 | TGTK132T1 | 21.5425 | TGTK132 132.00 | T1 | TGTK132 | TGTK132T1 | 21.5425 | 62127 | MTNH132T6
132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 115.4056 |  | PROT 33kV | 96173 | T5 | 48.8 | MTNH132 | MTNH132T5 | MELAKA | 11.3801 | 62127 | TGTK132 132.00 | T2 | TGTK132 | TGTK132T2 | 21.7807 | TGTK132 132.00 | T2 | TGTK132 | TGTK132T2 | 21.7807 | 62127 | MTNH132T5
132/11kV T1 & T2 | 31 & 32 | 21.521 |  | KLAT 11kV | #N/A | T4 | 48.8 | MTNH132 | MTNH132T4 | #N/A | #N/A | 62122 | VDOR132 132.00 | T1 | VDOR132 | VDOR132T1 | 12.69 | VDOR132 132.00 | T1 | VDOR132 | VDOR132T1 | 12.69 | 62122 | MTNH132T4
TPAU | 705 | 96 |  | TPAU, TEWA, UMKA, KCMT | 96173 | T3 | 48.8 | MTNH132 | MTNH132T3 | MELAKA | 2.8093 | 62122 | VDOR132 132.00 | T2 | VDOR132 | VDOR132T2 | 15.5097 | VDOR132 132.00 | T2 | VDOR132 | VDOR132T2 | 15.5097 | 62122 | MTNH132T3
TEWA 1 & 2 | 305 & 405 |  |  |  | 96173 | T2 | 48.8 | MTNH132 | MTNH132T2 | MELAKA | 6.2451 | 62122 | VDOR132 132.00 | T7 | VDOR132 | VDOR132T7 | 14.6066 | VDOR132 132.00 | T7 | VDOR132 | VDOR132T7 | 14.6066 | 62122 | MTNH132T2
132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 91.9517 |  | IMBI 33 kV | 96173 | T1 | 48.8 | MTNH132 | MTNH132T1 | MELAKA | 6.2285 | 562122 | VDOR_T7 132.00 | T7 | VDOR_T7 | VDOR_T7T7 | 0 | VDOR_T7 132.00 | T7 | VDOR_T7 | VDOR_T7T7 | 0 | 562122 | MTNH132T1
132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 148.4245 |  | KDSA 33kV | 96135 | T4 | 48.8 | TJID132 | TJID132T4 | NS | 19.9893 | 63106 | BDOR132 132.00 | T1 | BDOR132 | BDOR132T1 | 13.738 | BDOR132 132.00 | T1 | BDOR132 | BDOR132T1 | 13.738 | 63106 | TJID132T4
132/33kV T1 & T2 | 1T0 & 2T0 | 57.1456 |  | GWAY 33kV | 96135 | T3 | 48.8 | TJID132 | TJID132T3 | NS | 19.9675 | 63106 | BDOR132 132.00 | T2 | BDOR132 | BDOR132T2 | 6.7867 | BDOR132 132.00 | T2 | BDOR132 | BDOR132T2 | 6.7867 | 63106 | TJID132T3
VDOR/JNKO & NBTL Feeders | 105 & 205 | 144 |  | JNKO, VDOR, PBTR, NBTL | 96135 | T2 | 48.8 | TJID132 | TJID132T2 | NS | 7.8615 | 63106 | BDOR132 132.00 | T3 | BDOR132 | BDOR132T3 | 15.8017 | BDOR132 132.00 | T3 | BDOR132 | BDOR132T3 | 15.8017 | 63106 | TJID132T2
PBTR & NBTL | 105 & 205 |  |  |  | 96135 | T1 | 48.8 | TJID132 | TJID132T1 | NS | 11.1275 | 63106 | BDOR132 132.00 | T4 | BDOR132 | BDOR132T4 | 15.7965 | BDOR132 132.00 | T4 | BDOR132 | BDOR132T4 | 15.7965 | 63106 | TJID132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 80.5657 |  | SPNG 33kV | 96129 | T2 | 48.8 | TTJF132 | TTJF132T2 | NS | 14.9029 | 63153 | BMRH132 132.00 | T3 | BMRH132 | BMRH132T3 | 11.9486 | BMRH132 132.00 | T3 | BMRH132 | BMRH132T3 | 11.9486 | 63153 | TTJF132T2
MTIN & AMID | 505 & 605 |  |  |  | 96129 | T1 | 48.8 | TTJF132 | TTJF132T1 | NS | 14.8677 | 63153 | BMRH132 132.00 | T4 | BMRH132 | BMRH132T4 | 11.9787 | BMRH132 132.00 | T4 | BMRH132 | BMRH132T4 | 11.9787 | 63153 | TTJF132T1
MTIN 1 & 2 | 305 & 405 |  |  |  | 96193 | T5 | 48.8 | SSUN132 | SSUN132T5 | NS | 0 | 63151 | BSRI132 132.00 | T1 | BSRI132 | BSRI132T1 | 6.388 | BSRI132 132.00 | T1 | BSRI132 | BSRI132T1 | 6.388 | 63151 | SSUN132T5
KEST 1 & 2 | 105 & 205 |  |  |  | 96193 | T4 | 48.8 | SSUN132 | SSUN132T4 | NS | 0 | 63151 | BSRI132 132.00 | T2 | BSRI132 | BSRI132T2 | 15.8276 | BSRI132 132.00 | T2 | BSRI132 | BSRI132T2 | 15.8276 | 63151 | SSUN132T4
BHGT 1 & 2 | 305 & 405 |  |  |  | 96193 | T3 | 48.8 | SSUN132 | SSUN132T3 | NS | 0 | 63166 | BTNG132 132.00 | T1 | BTNG132 | BTNG132T1 | 14.1656 | BTNG132 132.00 | T1 | BTNG132 | BTNG132T1 | 14.1656 | 63166 | SSUN132T3
132/33kV T1 & T2 | 1T0 & 2T0 | 51.7312 |  | BMKM 33kV | 596193 | T2 | 48.8 | SSUN132 | SSUN132T2 | NS | 19.2717 | 63166 | BTNG132 132.00 | T2 | BTNG132 | BTNG132T2 | 14.3106 | BTNG132 132.00 | T2 | BTNG132 | BTNG132T2 | 14.3106 | 63166 | SSUN132T2
PLGI 1 & 2 | 905 & 1005 | 152 |  | KTGI, UTRM, PUBB, PLGI | 596193 | T1 | 48.8 | SSUN132 | SSUN132T1 | NS | 18.5282 | 63141 | CEND132 132.00 | T1 | CEND132 | CEND132T1 | 8.6226 | CEND132 132.00 | T1 | CEND132 | CEND132T1 | 8.6226 | 63141 | SSUN132T1
PUBB & KTGI | 505 & 605 |  |  |  | 96190 | T2 | 48.8 | STRA132 | STRA132T2 | NS | 6.9969 | 63141 | CEND132 132.00 | T2 | CEND132 | CEND132T2 | 8.604 | CEND132 132.00 | T2 | CEND132 | CEND132T2 | 8.604 | 63141 | STRA132T2
132/11kV T1 & T2 | 31 & 32 | 7.3649 |  | RNGM 11kV | 96190 | T1 | 48.8 | STRA132 | STRA132T1 | NS | 13.0794 | 63124 | GPRD132 132.00 | T1 | GPRD132 | GPRD132T1 | 5.5316 | GPRD132 132.00 | T1 | GPRD132 | GPRD132T1 | 5.5316 | 63124 | STRA132T1
KLID & NYOR | 105 & 205 | 111 |  | KLID, MSNG, TGMK & NYOR | 74120 | T2 | 48.8 | BNTA132 | BNTA132T2 | PAHANG | 2.7896 | 63124 | GPRD132 132.00 | T2 | GPRD132 | GPRD132T2 | 10.5393 | GPRD132 132.00 | T2 | GPRD132 | GPRD132T2 | 10.5393 | 63124 | BNTA132T2
132/11kV T1 & T2 | 31 & 32 | 33.8944 |  | KGAR 11kV | 74120 | T1 | 48.8 | BNTA132 | BNTA132T1 | PAHANG | 2.7813 | 63124 | GPRD132 132.00 | T3 | GPRD132 | GPRD132T3 | 51.2168 | GPRD132 132.00 | T3 | GPRD132 | GPRD132T3 | 51.2168 | 63124 | BNTA132T1
132/33kV T3 & T4 | 3T0 & 4T0 & 1W0 | 30.6965 |  | SIKD 33kV | 74121 | T4 | 48.8 | KLIP132 | KLIP132T4 | PAHANG | 12.4798 | 63124 | GPRD132 132.00 | T4 | GPRD132 | GPRD132T4 | 50.7798 | GPRD132 132.00 | T4 | GPRD132 | GPRD132T4 | 50.7798 | 63124 | KLIP132T4
132/33kV T3 & T4 | 3T0 & 4T0 | 36.7625 |  | LKDG 33kV | 74121 | T3 | 48.8 | KLIP132 | KLIP132T3 | PAHANG | 12.9841 | 63209 | GRIK275 275.00 | T1 | GRIK275 | GRIK275T1 | 9.6871 | GRIK275 275.00 | T1 | GRIK275 | GRIK275T1 | 9.6871 | 63209 | KLIP132T3
132/33kV T1 & T2 | 1T0&2T0 | 54.0023 |  | SJTC 33kV | 74121 | T2 | 48.8 | KLIP132 | KLIP132T2 | PAHANG | 5.9976 | 63176 | GTWN132 132.00 | T1 | GTWN132 | GTWN132T1 | 12.7636 | GTWN132 132.00 | T1 | GTWN132 | GTWN132T1 | 12.7636 | 63176 | KLIP132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 98.3955 |  | BBRU 33kV | 74121 | T1 | 48.8 | KLIP132 | KLIP132T1 | PAHANG | 11.407 | 63176 | GTWN132 132.00 | T2 | GTWN132 | GTWN132T2 | 11.9289 | GTWN132 132.00 | T2 | GTWN132 | GTWN132T2 | 11.9289 | 63176 | KLIP132T1
132/11kV T1 & T2 | 31 & 32 | 22.9899 |  | SMRK 11kV | 74123 | T7 | 48.8 | JNKA132 | JNKA132T7 | PAHANG | 5.542 | 63136 | HMLG132 132.00 | T1 | HMLG132 | HMLG132T1 | 32.5053 | HMLG132 132.00 | T1 | HMLG132 | HMLG132T1 | 32.5053 | 63136 | JNKA132T7
Hualon 1, 2 & 3 | 505605705 | 40 |  | HLNN | 74123 | T2 | 48.8 | JNKA132 | JNKA132T2 | PAHANG | 12.6745 | 63136 | HMLG132 132.00 | T2 | HMLG132 | HMLG132T2 | 32.3925 | HMLG132 132.00 | T2 | HMLG132 | HMLG132T2 | 32.3925 | 63136 | JNKA132T2
132/11kV T1 & T2 | 31 & 32 | 21.4779 |  | SELG 11kV | 74123 | T1 | 48.8 | JNKA132 | JNKA132T1 | PAHANG | 12.5948 | 63128 | KGJH132 132.00 | T1 | KGJH132 | KGJH132T1 | 9.1642 | KGJH132 132.00 | T1 | KGJH132 | KGJH132T1 | 9.1642 | 63128 | JNKA132T1
132/22kV T1 & T2 | 1T0 & 2T0 | 22.8338 |  | STUL 22kV | 74122 | T2 | 48.8 | JTUT132 | JTUT132T2 | PAHANG | 18.9921 | 63128 | KGJH132 132.00 | T2 | KGJH132 | KGJH132T2 | 8.3668 | KGJH132 132.00 | T2 | KGJH132 | KGJH132T2 | 8.3668 | 63128 | JTUT132T2
SGAD 1 & 2 | 105 & 205 | 105 |  | SGAD, PJML, PYSF, PSRI & SSLG | 74122 | T1 | 48.8 | JTUT132 | JTUT132T1 | PAHANG | 19.1629 | 63148 | KJWA132 132.00 | T1 | KJWA132 | KJWA132T1 | 7.3168 | KJWA132 132.00 | T1 | KJWA132 | KJWA132T1 | 7.3168 | 63148 | JTUT132T1
PJML & PYSF | 305 & 405 |  |  |  | 74151 | T4 | 48.8 | RBDR132 | RBDR132T4 | PAHANG | 0 | 63148 | KJWA132 132.00 | T2 | KJWA132 | KJWA132T2 | 6.6272 | KJWA132 132.00 | T2 | KJWA132 | KJWA132T2 | 6.6272 | 63148 | RBDR132T4
132/11kV T1 & T2 | 31 & 32 | 10 |  | MSNG 11kV | 74151 | T3 | 48.8 | RBDR132 | RBDR132T3 | PAHANG | 0 | 63138 | KKSR132 132.00 | T1 | KKSR132 | KKSR132T1 | 11.696 | KKSR132 132.00 | T1 | KKSR132 | KKSR132T1 | 11.696 | 63138 | RBDR132T3
132/11kV T1 & T2 | 31 & 32 | 22 |  | SLNG 11kV | 74151 | T2 | 48.8 | RBDR132 | RBDR132T2 | PAHANG | 11.0332 | 63138 | KKSR132 132.00 | T2 | KKSR132 | KKSR132T2 | 8.2239 | KKSR132 132.00 | T2 | KKSR132 | KKSR132T2 | 8.2239 | 63138 | RBDR132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 90 |  | BTGH 33kV | 74151 | T1 | 48.8 | RBDR132 | RBDR132T1 | PAHANG | 11.7011 | 63155 | KLBG132 132.00 | T1 | KLBG132 | KLBG132T1 | 15.3295 | KLBG132 132.00 | T1 | KLBG132 | KLBG132T1 | 15.3295 | 63155 | RBDR132T1
132/11kV T1 & T2 | 31 & 32 | 16 |  | BCVS 11kV | 62105 | T4 | 48.8 | ATJN132 | ATJN132T4 | P PINANG | 23.0864 | 63155 | KLBG132 132.00 | T2 | KLBG132 | KLBG132T2 | 15.1918 | KLBG132 132.00 | T2 | KLBG132 | KLBG132T2 | 15.1918 | 63155 | ATJN132T4
132/33kV T3 & T4 | 3T0 & 4T0 | 90 |  | HKCK 33kV | 62105 | T3 | 48.8 | ATJN132 | ATJN132T3 | P PINANG | 22.4579 | 63155 | KLBG132 132.00 | T3 | KLBG132 | KLBG132T3 | 11.2807 | KLBG132 132.00 | T3 | KLBG132 | KLBG132T3 | 11.2807 | 63155 | ATJN132T3
132/33kV T3 &T4 | 3T0 & 4T0 | 22 |  | SLNG 33kV | 61109 | T2 | 48.8 | GRUN132 | GRUN132T2 | KEDAH | 4.6991 | 63155 | KLBG132 132.00 | T4 | KLBG132 | KLBG132T4 | 11.2352 | KLBG132 132.00 | T4 | KLBG132 | KLBG132T4 | 11.2352 | 63155 | GRUN132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 86 |  | BTBN 33kV | 61109 | T1 | 48.8 | GRUN132 | GRUN132T1 | KEDAH | 4.7177 | 63104 | KMPR132 132.00 | T1 | KMPR132 | KMPR132T1 | 0 | KMPR132 132.00 | T1 | KMPR132 | KMPR132T1 | 0 | 63104 | GRUN132T1
132/11kV T1 & T2 | 31 & 32 | 14 |  | HKCK 11kV | 61107 | T2 | 48.8 | JENG132 | JENG132T2 | KEDAH | 13.914 | 63104 | KMPR132 132.00 | T2 | KMPR132 | KMPR132T2 | 24.0919 | KMPR132 132.00 | T2 | KMPR132 | KMPR132T2 | 24.0919 | 63104 | JENG132T2
132/33kV T1 & T2 | 1T0 & 2T0 | 74 |  | TJYA 33kV | 61107 | T1 | 48.8 | JENG132 | JENG132T1 | KEDAH | 14.4773 | 63104 | KMPR132 132.00 | T3 | KMPR132 | KMPR132T3 | 15.3005 | KMPR132 132.00 | T3 | KMPR132 | KMPR132T3 | 15.3005 | 63104 | JENG132T1
132/33kV T1 & T2 | 1T0 & 2T0 | 26 |  | SDAI 33kV | 63129 | T2 | 48.7 | LMUT132 | LMUT132T2 | PERAK | 43.2455 | 63104 | KMPR132 132.00 | T4 | KMPR132 | KMPR132T4 | 15.5056 | KMPR132 132.00 | T4 | KMPR132 | KMPR132T4 | 15.5056 | 63104 | LMUT132T2
132/22kV T1 & T2 | 1T0 & 2T0 | 22 |  | UTRM 22kV | 63129 | T1 | 48.7 | LMUT132 | LMUT132T1 | PERAK | 42.3395 | 63119 | KMTG132 132.00 | T1 | KMTG132 | KMTG132T1 | 10.0278 | KMTG132 132.00 | T1 | KMTG132 | KMTG132T1 | 10.0278 | 63119 | LMUT132T1
132/33kV T3 & T4 | 3T0 & 4T0 | 64 |  | UTRM 33kV | 63131 | T4 | 48.7 | LMTM132 | LMTM132T4 | PERAK | 39.8843 | 63119 | KMTG132 132.00 | T2 | KMTG132 | KMTG132T2 | 10.0702 | KMTG132 132.00 | T2 | KMTG132 | KMTG132T2 | 10.0702 | 63119 | LMTM132T4
[5 empty] | 63131 | T3 | 48.7 | LMTM132 | LMTM132T3 | PERAK | 41.5587 | 63119 | KMTG132 132.00 | T3 | KMTG132 | KMTG132T3 | 6.5547 | KMTG132 132.00 | T3 | KMTG132 | KMTG132T3 | 6.5547 | 63119 | LMTM132T3
[5 empty] | 88129 | T2 | 48.7 | MDAM132 | MDAM132T2 | WPKL | 17.3322 | 63119 | KMTG132 132.00 | T4 | KMTG132 | KMTG132T4 | 8.4807 | KMTG132 132.00 | T4 | KMTG132 | KMTG132T4 | 8.4807 | 63119 | MDAM132T2
[5 empty] | 88129 | T1 | 48.7 | MDAM132 | MDAM132T1 | WPKL | 18.2683 | 63173 | KVRT132 132.00 | T1 | KVRT132 | KVRT132T1 | 12.8485 | KVRT132 132.00 | T1 | KVRT132 | KVRT132T1 | 12.8485 | 63173 | MDAM132T1
[5 empty] | 88194 | T4 | 48.7 | BCVS132 | BCVS132T4 | SELANGOR | 43.8937 | 63173 | KVRT132 132.00 | T2 | KVRT132 | KVRT132T2 | 10.9721 | KVRT132 132.00 | T2 | KVRT132 | KVRT132T2 | 10.9721 | 63173 | BCVS132T4
[5 empty] | 88194 | T3 | 48.7 | BCVS132 | BCVS132T3 | SELANGOR | 43.4019 | 63173 | KVRT132 132.00 | T3 | KVRT132 | KVRT132T3 | 33.9395 | KVRT132 132.00 | T3 | KVRT132 | KVRT132T3 | 33.9395 | 63173 | BCVS132T3
[5 empty] | 97119 | T2 | 48.7 | PRJA132 | PRJA132T2 | JOHOR | 0 | 63173 | KVRT132 132.00 | T4 | KVRT132 | KVRT132T4 | 33.9333 | KVRT132 132.00 | T4 | KVRT132 | KVRT132T4 | 33.9333 | 63173 | PRJA132T2
[5 empty] | 97119 | T1 | 48.7 | PRJA132 | PRJA132T1 | JOHOR | 20.4677 | 63131 | LMTM132 132.00 | T1 | LMTM132 | LMTM132T1 | 12.4063 | LMTM132 132.00 | T1 | LMTM132 | LMTM132T1 | 12.4063 | 63131 | PRJA132T1
[5 empty] | 96405 | T4 | 48.7 | MCOP132 | MCOP132T4 | MELAKA | 37.7336 | 63131 | LMTM132 132.00 | T2 | LMTM132 | LMTM132T2 | 12.3649 | LMTM132 132.00 | T2 | LMTM132 | LMTM132T2 | 12.3649 | 63131 | MCOP132T4
[5 empty] | 96405 | T3 | 48.7 | MCOP132 | MCOP132T3 | MELAKA | 37.6735 | 63131 | LMTM132 132.00 | T3 | LMTM132 | LMTM132T3 | 41.5587 | LMTM132 132.00 | T3 | LMTM132 | LMTM132T3 | 41.5587 | 63131 | MCOP132T3
[5 empty] | 96405 | T2 | 48.7 | MCOP132 | MCOP132T2 | MELAKA | 10.4834 | 63131 | LMTM132 132.00 | T4 | LMTM132 | LMTM132T4 | 39.8843 | LMTM132 132.00 | T4 | LMTM132 | LMTM132T4 | 39.8843 | 63131 | MCOP132T2
[5 empty] | 96405 | T1 | 48.7 | MCOP132 | MCOP132T1 | MELAKA | 13.2057 | 63129 | LMUT132 132.00 | T1 | LMUT132 | LMUT132T1 | 42.3395 | LMUT132 132.00 | T1 | LMUT132 | LMUT132T1 | 42.3395 | 63129 | MCOP132T1
[5 empty] | 96124 | F2 | 48.7 | XNYI132 | XNYI132F2 | MELAKA | 27.8171 | 63129 | LMUT132 132.00 | T2 | LMUT132 | LMUT132T2 | 43.2455 | LMUT132 132.00 | T2 | LMUT132 | LMUT132T2 | 43.2455 | 63129 | XNYI132F2
[5 empty] | 96124 | F1 | 48.7 | XNYI132 | XNYI132F1 | MELAKA | 9.9734 | 63129 | LMUT132 132.00 | T3 | LMUT132 | LMUT132T3 | 27.7783 | LMUT132 132.00 | T3 | LMUT132 | LMUT132T3 | 27.7783 | 63129 | XNYI132F1
[5 empty] | 97117 | T2 | 48.7 | TKID132 | TKID132T2 | MELAKA | 8.3958 | 63160 | MERY132 132.00 | T1 | MERY132 | MERY132T1 | 3.6346 | MERY132 132.00 | T1 | MERY132 | MERY132T1 | 3.6346 | 63160 | TKID132T2
[5 empty] | 97117 | T1 | 48.7 | TKID132 | TKID132T1 | MELAKA | 8.4725 | 63160 | MERY132 132.00 | T2 | MERY132 | MERY132T2 | 3.6139 | MERY132 132.00 | T2 | MERY132 | MERY132T2 | 3.6139 | 63160 | TKID132T1
[5 empty] | 97128 | T4 | 48.7 | TKAK132 | TKAK132T4 | JOHOR | 11.2041 | 63146 | MLBU132 132.00 | T1 | MLBU132 | MLBU132T1 | 8.4952 | MLBU132 132.00 | T1 | MLBU132 | MLBU132T1 | 8.4952 | 63146 | TKAK132T4
[5 empty] | 97128 | T3 | 48.7 | TKAK132 | TKAK132T3 | JOHOR | 11.1461 | 63146 | MLBU132 132.00 | T2 | MLBU132 | MLBU132T2 | 12.5813 | MLBU132 132.00 | T2 | MLBU132 | MLBU132T2 | 12.5813 | 63146 | TKAK132T3
[5 empty] | 97150 | T2 | 48.7 | JMTH132 | JMTH132T2 | JOHOR | 7.5384 | 63146 | MLBU132 132.00 | T3 | MLBU132 | MLBU132T3 | 34.4842 | MLBU132 132.00 | T3 | MLBU132 | MLBU132T3 | 34.4842 | 63146 | JMTH132T2
[5 empty] | 97150 | T1 | 48.7 | JMTH132 | JMTH132T1 | JOHOR | 6.389 | 63146 | MLBU132 132.00 | T4 | MLBU132 | MLBU132T4 | 34.6333 | MLBU132 132.00 | T4 | MLBU132 | MLBU132T4 | 34.6333 | 63146 | JMTH132T1
[5 empty] | 97141 | T2 | 48.7 | SGMT132 | SGMT132T2 | JOHOR | 9.8466 | 63142 | NKAN132 132.00 | T1 | NKAN132 | NKAN132T1 | 14.7455 | NKAN132 132.00 | T1 | NKAN132 | NKAN132T1 | 14.7455 | 63142 | SGMT132T2
[5 empty] | 97141 | T1 | 48.7 | SGMT132 | SGMT132T1 | JOHOR | 7.9878 | 63142 | NKAN132 132.00 | T2 | NKAN132 | NKAN132T2 | 14.8076 | NKAN132 132.00 | T2 | NKAN132 | NKAN132T2 | 14.8076 | 63142 | SGMT132T1
[5 empty] | 97182 | T4 | 48.7 | BSPT132 | BSPT132T4 | JOHOR | 15.5418 | 63118 | PBTR132 132.00 | T1 | PBTR132 | PBTR132T1 | 19.1557 | PBTR132 132.00 | T1 | PBTR132 | PBTR132T1 | 19.1557 | 63118 | BSPT132T4
[5 empty] | 97182 | T3 | 48.7 | BSPT132 | BSPT132T3 | JOHOR | 15.3606 | 63118 | PBTR132 132.00 | T2 | PBTR132 | PBTR132T2 | 22.1845 | PBTR132 132.00 | T2 | PBTR132 | PBTR132T2 | 22.1845 | 63118 | BSPT132T3
[5 empty] | 97182 | T2 | 48.7 | BSPT132 | BSPT132T2 | JOHOR | 9.7906 | 63120 | PKCB132 132.00 | T1 | PKCB132 | PKCB132T1 | 2.4552 | PKCB132 132.00 | T1 | PKCB132 | PKCB132T1 | 2.4552 | 63120 | BSPT132T2
[5 empty] | 97182 | T1 | 48.7 | BSPT132 | BSPT132T1 | JOHOR | 9.7761 | 63120 | PKCB132 132.00 | T2 | PKCB132 | PKCB132T2 | 2.4179 | PKCB132 132.00 | T2 | PKCB132 | PKCB132T2 | 2.4179 | 63120 | BSPT132T1
[5 empty] | 97174 | T2 | 48.7 | BKPG132 | BKPG132T2 | JOHOR | 3.8427 | 63145 | PKID132 132.00 | T1 | PKID132 | PKID132T1 | 5.4146 | PKID132 132.00 | T1 | PKID132 | PKID132T1 | 5.4146 | 63145 | BKPG132T2
[5 empty] | 97174 | T1 | 48.7 | BKPG132 | BKPG132T1 | JOHOR | 3.8365 | 63145 | PKID132 132.00 | T2 | PKID132 | PKID132T2 | 9.6612 | PKID132 132.00 | T2 | PKID132 | PKID132T2 | 9.6612 | 63145 | BKPG132T1
[5 empty] | 97148 | T4 | 48.7 | CAAH132 | CAAH132T4 | JOHOR | 9.9108 | 63145 | PKID132 132.00 | T3 | PKID132 | PKID132T3 | 12.6652 | PKID132 132.00 | T3 | PKID132 | PKID132T3 | 12.6652 | 63145 | CAAH132T4
[5 empty] | 97148 | T3 | 48.7 | CAAH132 | CAAH132T3 | JOHOR | 9.9708 | 63145 | PKID132 132.00 | T4 | PKID132 | PKID132T4 | 12.6579 | PKID132 132.00 | T4 | PKID132 | PKID132T4 | 12.6579 | 63145 | CAAH132T3
[5 empty] | 96138 | T4 | 48.7 | BAHA132 | BAHA132T4 | NS | 5.4674 | 63133 | PKLN132 132.00 | T1 | PKLN132 | PKLN132T1 | 6.7546 | PKLN132 132.00 | T1 | PKLN132 | PKLN132T1 | 6.7546 | 63133 | BAHA132T4
[5 empty] | 96138 | T3 | 48.7 | BAHA132 | BAHA132T3 | NS | 5.4177 | 63133 | PKLN132 132.00 | T2 | PKLN132 | PKLN132T2 | 16.7699 | PKLN132 132.00 | T2 | PKLN132 | PKLN132T2 | 16.7699 | 63133 | BAHA132T3
[5 empty] | 96138 | T2 | 48.7 | BAHA132 | BAHA132T2 | NS | 12.3835 | 63133 | PKLN132 132.00 | T3 | PKLN132 | PKLN132T3 | 35.4928 | PKLN132 132.00 | T3 | PKLN132 | PKLN132T3 | 35.4928 | 63133 | BAHA132T2
[5 empty] | 96138 | T1 | 48.7 | BAHA132 | BAHA132T1 | NS | 12.4001 | 63133 | PKLN132 132.00 | T4 | PKLN132 | PKLN132T4 | 35.3654 | PKLN132 132.00 | T4 | PKLN132 | PKLN132T4 | 35.3654 | 63133 | BAHA132T1
[5 empty] | 96151 | T2 | 48.7 | NSCI132 | NSCI132T2 | NS | 13.5692 | 63147 | SBGS132 132.00 | T1 | SBGS132 | SBGS132T1 | 6.4284 | SBGS132 132.00 | T1 | SBGS132 | SBGS132T1 | 6.4284 | 63147 | NSCI132T2
[5 empty] | 96151 | T1 | 48.7 | NSCI132 | NSCI132T1 | NS | 12.6745 | 63147 | SBGS132 132.00 | T2 | SBGS132 | SBGS132T2 | 6.3932 | SBGS132 132.00 | T2 | SBGS132 | SBGS132T2 | 6.3932 | 63147 | NSCI132T1
[5 empty] | 96113 | T4 | 48.7 | UPSR132 | UPSR132T4 | MELAKA | 25.6421 | 63147 | SBGS132 132.00 | T3 | SBGS132 | SBGS132T3 | 0 | SBGS132 132.00 | T3 | SBGS132 | SBGS132T3 | 0 | 63147 | UPSR132T4
[5 empty] | 96113 | T3 | 48.7 | UPSR132 | UPSR132T3 | MELAKA | 25.6545 | 63147 | SBGS132 132.00 | T4 | SBGS132 | SBGS132T4 | 11.9393 | SBGS132 132.00 | T4 | SBGS132 | SBGS132T4 | 11.9393 | 63147 | UPSR132T3
[5 empty] | 96113 | T2 | 48.7 | UPSR132 | UPSR132T2 | MELAKA | 11.6318 | 63125 | SIHY132 132.00 | T1 | SIHY132 | SIHY132T1 | 0.1139 | SIHY132 132.00 | T1 | SIHY132 | SIHY132T1 | 0.1139 | 63125 | UPSR132T2
[5 empty] | 96113 | T1 | 48.7 | UPSR132 | UPSR132T1 | MELAKA | 7.2423 | 63125 | SIHY132 132.00 | T2 | SIHY132 | SIHY132T2 | 0.1035 | SIHY132 132.00 | T2 | SIHY132 | SIHY132T2 | 0.1035 | 63125 | UPSR132T1
[5 empty] | 96125 | T2 | 48.7 | NLAI132 | NLAI132T2 | NS | 5.0035 | 63111 | SIKD132 132.00 | T1 | SIKD132 | SIKD132T1 | 18.1492 | SIKD132 132.00 | T1 | SIKD132 | SIKD132T1 | 18.1492 | 63111 | NLAI132T2
[5 empty] | 96125 | T1 | 48.7 | NLAI132 | NLAI132T1 | NS | 9.9377 | 63111 | SIKD132 132.00 | T2 | SIKD132 | SIKD132T2 | 18.1264 | SIKD132 132.00 | T2 | SIKD132 | SIKD132T2 | 18.1264 | 63111 | NLAI132T1
[5 empty] | 51048 | T3 | 48.7 | BTGA132 | BTGA132T3 | SELANGOR | 0 | 63111 | SIKD132 132.00 | T3 | SIKD132 | SIKD132T3 | 23.8703 | SIKD132 132.00 | T3 | SIKD132 | SIKD132T3 | 23.8703 | 63111 | BTGA132T3
[5 empty] | 51048 | T2 | 48.7 | BTGA132 | BTGA132T2 | SELANGOR | 19.0863 | 63111 | SIKD132 132.00 | T4 | SIKD132 | SIKD132T4 | 23.9211 | SIKD132 132.00 | T4 | SIKD132 | SIKD132T4 | 23.9211 | 63111 | BTGA132T2
[5 empty] | 51048 | T1 | 48.7 | BTGA132 | BTGA132T1 | SELANGOR | 18.814 | 63157 | SRVR132 132.00 | T5 | SRVR132 | SRVR132T5 | 7.6938 | SRVR132 132.00 | T5 | SRVR132 | SRVR132T5 | 7.6938 | 63157 | BTGA132T1
[5 empty] | 51035 | T2 | 48.7 | BBDG132 | BBDG132T2 | SELANGOR | 27.6499 | 63157 | SRVR132 132.00 | T6 | SRVR132 | SRVR132T6 | 7.7031 | SRVR132 132.00 | T6 | SRVR132 | SRVR132T6 | 7.7031 | 63157 | BBDG132T2
[5 empty] | 51035 | T1 | 48.7 | BBDG132 | BBDG132T1 | SELANGOR | 27.7327 | 463159 | SSLS132 132.00 | T1 | SSLS132 | SSLS132T1 | 15.5324 | SSLS132 132.00 | T1 | SSLS132 | SSLS132T1 | 15.5324 | 463159 | BBDG132T1
[5 empty] | 51052 | T2 | 48.7 | RSID132 | RSID132T2 | SELANGOR | 16.3112 | 63140 | SSPT132 132.00 | T1 | SSPT132 | SSPT132T1 | 13.1084 | SSPT132 132.00 | T1 | SSPT132 | SSPT132T1 | 13.1084 | 63140 | RSID132T2
[5 empty] | 51052 | T2 | 48.7 | RSID132 | RSID132T2 | SELANGOR | 16.3112 | 63140 | SSPT132 132.00 | T2 | SSPT132 | SSPT132T2 | 13.0877 | SSPT132 132.00 | T2 | SSPT132 | SSPT132T2 | 13.0877 | 63140 | RSID132T2
[5 empty] | 97105 | T2 | 48.6 | GRSK132 | GRSK132T2 | JOHOR | 11.9807 | 63126 | SYPS132 132.00 | T1 | SYPS132 | SYPS132T1 | 0.3552 | SYPS132 132.00 | T1 | SYPS132 | SYPS132T1 | 0.3552 | 63126 | GRSK132T2
[5 empty] | 97105 | T1 | 48.6 | GRSK132 | GRSK132T1 | JOHOR | 12.0087 | 63126 | SYPS132 132.00 | T2 | SYPS132 | SYPS132T2 | 0.3572 | SYPS132 132.00 | T2 | SYPS132 | SYPS132T2 | 0.3572 | 63126 | GRSK132T1
[5 empty] | 97132 | T2 | 48.6 | KPTR132 | KPTR132T2 | JOHOR | 11.7488 | 63134 | TASK132 132.00 | T1 | TASK132 | TASK132T1 | 4.8461 | TASK132 132.00 | T1 | TASK132 | TASK132T1 | 4.8461 | 63134 | KPTR132T2
[5 empty] | 97132 | T1 | 48.6 | KPTR132 | KPTR132T1 | JOHOR | 11.7539 | 63134 | TASK132 132.00 | T2 | TASK132 | TASK132T2 | 4.7219 | TASK132 132.00 | T2 | TASK132 | TASK132T2 | 4.7219 | 63134 | KPTR132T1
[5 empty] | 97113 | T8 | 48.6 | SDAI132 | SDAI132T8 | JOHOR | 0.6741 | 63134 | TASK132 132.00 | T3 | TASK132 | TASK132T3 | 9.4603 | TASK132 132.00 | T3 | TASK132 | TASK132T3 | 9.4603 | 63134 | SDAI132T8
[5 empty] | 97113 | T7 | 48.6 | SDAI132 | SDAI132T7 | JOHOR | 0.6275 | 63134 | TASK132 132.00 | T4 | TASK132 | TASK132T4 | 11.7529 | TASK132 132.00 | T4 | TASK132 | TASK132T4 | 11.7529 | 63134 | SDAI132T7
[5 empty] | 97185 | T2 | 48.6 | LKIN132 | LKIN132T2 | JOHOR | 11.7995 | 63135 | TCMT132 132.00 | T1 | TCMT132 | TCMT132T1 | 6.563 | TCMT132 132.00 | T1 | TCMT132 | TCMT132T1 | 6.563 | 63135 | LKIN132T2
[5 empty] | 97185 | T1 | 48.6 | LKIN132 | LKIN132T1 | JOHOR | 11.7415 | 63135 | TCMT132 132.00 | T2 | TCMT132 | TCMT132T2 | 9.917 | TCMT132 132.00 | T2 | TCMT132 | TCMT132T2 | 9.917 | 63135 | LKIN132T1
[5 empty] | 74127 | T2 | 48.6 | SONG132 | SONG132T2 | PAHANG | 7.612 | 63135 | TCMT132 132.00 | T3 | TCMT132 | TCMT132T3 | 2.5069 | TCMT132 132.00 | T3 | TCMT132 | TCMT132T3 | 2.5069 | 63135 | SONG132T2
[5 empty] | 74127 | T1 | 48.6 | SONG132 | SONG132T1 | PAHANG | 14.467 | 63135 | TCMT132 132.00 | T4 | TCMT132 | TCMT132T4 | 2.5173 | TCMT132 132.00 | T4 | TCMT132 | TCMT132T4 | 2.5173 | 63135 | SONG132T1
[5 empty] | 74117 | T2 | 48.6 | MTKB132 | MTKB132T2 | PAHANG | 22.578 | 63150 | TINE132 132.00 | T1 | TINE132 | TINE132T1 | 8.6288 | TINE132 132.00 | T1 | TINE132 | TINE132T1 | 8.6288 | 63150 | MTKB132T2
[5 empty] | 74117 | T1 | 48.6 | MTKB132 | MTKB132T1 | PAHANG | 0 | 63150 | TINE132 132.00 | T2 | TINE132 | TINE132T2 | 8.5884 | TINE132 132.00 | T2 | TINE132 | TINE132T2 | 8.5884 | 63150 | MTKB132T1
[5 empty] | 74144 | T4 | 48.6 | TMID132 | TMID132T4 | PAHANG | 0 | 63130 | TINT132 132.00 | T1 | TINT132 | TINT132T1 | 10.6242 | TINT132 132.00 | T1 | TINT132 | TINT132T1 | 10.6242 | 63130 | TMID132T4
[5 empty] | 74144 | T3 | 48.6 | TMID132 | TMID132T3 | PAHANG | 0 | 63130 | TINT132 132.00 | T2 | TINT132 | TINT132T2 | 10.4544 | TINT132 132.00 | T2 | TINT132 | TINT132T2 | 10.4544 | 63130 | TMID132T3
[5 empty] | 74144 | T2 | 48.6 | TMID132 | TMID132T2 | PAHANG | 9.1155 | 563130 | TINT132R 132.00 | T3 | TINT132 | TINT132T3 | 6.4719 | TINT132R 132.00 | T3 | TINT132 | TINT132T3 | 6.4719 | 563130 | TMID132T2
[5 empty] | 74144 | T1 | 48.6 | TMID132 | TMID132T1 | PAHANG | 9.0399 | 63206 | TMGR275 275.00 | T1 | TMGR275 | TMGR275T1 | 6.0473 | TMGR275 275.00 | T1 | TMGR275 | TMGR275T1 | 6.0473 | 63206 | TMID132T1
[5 empty] | 74147 | F1 | 48.6 | MNID132 | MNID132F1 | PAHANG | 0.321 | 63127 | TMOH132 132.00 | T3 | TMOH132 | TMOH132T3 | 11.3905 | TMOH132 132.00 | T3 | TMOH132 | TMOH132T3 | 11.3905 | 63127 | MNID132F1
[5 empty] | 62118 | T3 | 48.6 | GLGR132 | GLGR132T3 | P PINANG | 21.4069 | 63127 | TMOH132 132.00 | T4 | TMOH132 | TMOH132T4 | 11.2144 | TMOH132 132.00 | T4 | TMOH132 | TMOH132T4 | 11.2144 | 63127 | GLGR132T3
[5 empty] | 62118 | T2 | 48.6 | GLGR132 | GLGR132T2 | P PINANG | 21.3737 | 63154 | TPID132 132.00 | T1 | TPID132 | TPID132T1 | 12.5244 | TPID132 132.00 | T1 | TPID132 | TPID132T1 | 12.5244 | 63154 | GLGR132T2
[5 empty] | 62118 | T1 | 48.6 | GLGR132 | GLGR132T1 | P PINANG | 19.1961 | 63154 | TPID132 132.00 | T2 | TPID132 | TPID132T2 | 12.6248 | TPID132 132.00 | T2 | TPID132 | TPID132T2 | 12.6248 | 63154 | GLGR132T1
[5 empty] | 62110 | T2 | 48.6 | BMTR132 | BMTR132T2 | P PINANG | 57.494 | 63154 | TPID132 132.00 | T3 | TPID132 | TPID132T3 | 34.218 | TPID132 132.00 | T3 | TPID132 | TPID132T3 | 34.218 | 63154 | BMTR132T2
[5 empty] | 62110 | T1 | 48.6 | BMTR132 | BMTR132T1 | P PINANG | 62.7419 | 63154 | TPID132 132.00 | T4 | TPID132 | TPID132T4 | 33.9716 | TPID132 132.00 | T4 | TPID132 | TPID132T4 | 33.9716 | 63154 | BMTR132T1
[5 empty] | 62120 | T2 | 48.6 | BKWS132 | BKWS132T2 | P PINANG | 54.3657 | 63121 | TPNG132 132.00 | T1 | TPNG132 | TPNG132T1 | 9.5307 | TPNG132 132.00 | T1 | TPNG132 | TPNG132T1 | 9.5307 | 63121 | BKWS132T2
[5 empty] | 62120 | T1 | 48.6 | BKWS132 | BKWS132T1 | P PINANG | 55.8776 | 563121 | TPNG132R 132.00 | T2 | TPNG132 | TPNG132T2 | 15.5169 | TPNG132R 132.00 | T2 | TPNG132 | TPNG132T2 | 15.5169 | 563121 | BKWS132T1
[5 empty] | 61137 | T4 | 48.6 | KGAR132 | KGAR132T4 | PERLIS | 10.9504 | 74212 | UJLI275 275.00 | T1 | UJLI275 | UJLI275T1 | 0.8305 | UJLI275 275.00 | T1 | UJLI275 | UJLI275T1 | 0.8305 | 74212 | KGAR132T4
[5 empty] | 61137 | T3 | 48.6 | KGAR132 | KGAR132T3 | PERLIS | 7.408 | 74212 | UJLI275 275.00 | T2 | UJLI275 | UJLI275T2 | 0.8398 | UJLI275 275.00 | T2 | UJLI275 | UJLI275T2 | 0.8398 | 74212 | KGAR132T3
[5 empty] | 51041 | T4 | 48.6 | SHAW132 | SHAW132T4 | SELANGOR | 28.4565 | 51061 | ABBA132 132.00 | T1 | ABBA132 | ABBA132T1 | 3.6853 | ABBA132 132.00 | T1 | ABBA132 | ABBA132T1 | 3.6853 | 51061 | SHAW132T4
[5 empty] | 51041 | T3 | 48.6 | SHAW132 | SHAW132T3 | SELANGOR | 28.5911 | 51061 | ABBA132 132.00 | T2 | ABBA132 | ABBA132T2 | 9.9542 | ABBA132 132.00 | T2 | ABBA132 | ABBA132T2 | 9.9542 | 51061 | SHAW132T3
[5 empty] | 51041 | T2 | 48.6 | SHAW132 | SHAW132T2 | SELANGOR | 5.8288 | 51061 | ABBA132 132.00 | T3 | ABBA132 | ABBA132T3 | 27.8259 | ABBA132 132.00 | T3 | ABBA132 | ABBA132T3 | 27.8259 | 51061 | SHAW132T2
[5 empty] | 51041 | T1 | 48.6 | SHAW132 | SHAW132T1 | SELANGOR | 9.2294 | 51061 | ABBA132 132.00 | T4 | ABBA132 | ABBA132T4 | 27.5484 | ABBA132 132.00 | T4 | ABBA132 | ABBA132T4 | 27.5484 | 51061 | SHAW132T1
[5 empty] | 51051 | T4 | 48.6 | TPGR132 | TPGR132T4 | SELANGOR | 45.5454 | 51019 | ADAM132 132.00 | T1 | ADAM132 | ADAM132T1 | 12.9334 | ADAM132 132.00 | T1 | ADAM132 | ADAM132T1 | 12.9334 | 51019 | TPGR132T4
[5 empty] | 51051 | T3 | 48.6 | TPGR132 | TPGR132T3 | SELANGOR | 45.2886 | 51019 | ADAM132 132.00 | T2 | ADAM132 | ADAM132T2 | 12.4084 | ADAM132 132.00 | T2 | ADAM132 | ADAM132T2 | 12.4084 | 51019 | TPGR132T3
[5 empty] | 51003 | T3 | 48.6 | SHAN132 | SHAN132T3 | SELANGOR | 0 | 51028 | AHTM132 132.00 | T1 | AHTM132 | AHTM132T1 | 43.4909 | AHTM132 132.00 | T1 | AHTM132 | AHTM132T1 | 43.4909 | 51028 | SHAN132T3
[5 empty] | 51003 | T2 | 48.6 | SHAN132 | SHAN132T2 | SELANGOR | 0.007 | 51028 | AHTM132 132.00 | T2 | AHTM132 | AHTM132T2 | 44.3266 | AHTM132 132.00 | T2 | AHTM132 | AHTM132T2 | 44.3266 | 51028 | SHAN132T2
[5 empty] | 51003 | T1 | 48.6 | SHAN132 | SHAN132T1 | SELANGOR | 0 | 51043 | BARG132 132.00 | T1 | BARG132 | BARG132T1 | 12.2593 | BARG132 132.00 | T1 | BARG132 | BARG132T1 | 12.2593 | 51043 | SHAN132T1
[5 empty] | 51002 | T2 | 48.6 | SHLB132 | SHLB132T2 | SELANGOR | 27.5132 | 51043 | BARG132 132.00 | T2 | BARG132 | BARG132T2 | 5.746 | BARG132 132.00 | T2 | BARG132 | BARG132T2 | 5.746 | 51043 | SHLB132T2
[5 empty] | 51002 | T1 | 48.6 | SHLB132 | SHLB132T1 | SELANGOR | 27.4096 | 51043 | BARG132 132.00 | T3 | BARG132 | BARG132T3 | 18.202 | BARG132 132.00 | T3 | BARG132 | BARG132T3 | 18.202 | 51043 | SHLB132T1
[5 empty] | 51037 | T2 | 48.6 | BBTC132 | BBTC132T2 | SELANGOR | 38.0753 | 51043 | BARG132 132.00 | T4 | BARG132 | BARG132T4 | 17.998 | BARG132 132.00 | T4 | BARG132 | BARG132T4 | 17.998 | 51043 | BBTC132T2
[5 empty] | 51037 | T1 | 48.6 | BBTC132 | BBTC132T1 | SELANGOR | 38.708 | 51035 | BBDG132 132.00 | T1 | BBDG132 | BBDG132T1 | 27.7327 | BBDG132 132.00 | T1 | BBDG132 | BBDG132T1 | 27.7327 | 51035 | BBTC132T1
[5 empty] | 61115 | T2 | 48.6 | BDNG132 | BDNG132T2 | KEDAH | 18.7487 | 51035 | BBDG132 132.00 | T2 | BBDG132 | BBDG132T2 | 27.6499 | BBDG132 132.00 | T2 | BBDG132 | BBDG132T2 | 27.6499 | 51035 | BDNG132T2
[5 empty] | 61115 | T1 | 48.6 | BDNG132 | BDNG132T1 | KEDAH | 21.703 | 551035 | BBDG132_T 132.00 | T7 | BBDG132 | BBDG132T7 | 18.3387 | BBDG132_T 132.00 | T7 | BBDG132 | BBDG132T7 | 18.3387 | 551035 | BDNG132T1
[5 empty] | 88111 | T2 | 48.6 | KULN132 | KULN132T2 | WPKL | 38.2026 | 51071 | BBST132 132.00 | T1 | BBST132 | BBST132T1 | 5.5306 | BBST132 132.00 | T1 | BBST132 | BBST132T1 | 5.5306 | 51071 | KULN132T2
[5 empty] | 88111 | T1 | 48.6 | KULN132 | KULN132T1 | WPKL | 38.272 | 51071 | BBST132 132.00 | T2 | BBST132 | BBST132T2 | 3.9287 | BBST132 132.00 | T2 | BBST132 | BBST132T2 | 3.9287 | 51071 | KULN132T1
[5 empty] | 75103 | T2 | 48.6 | DGUN132 | DGUN132T2 | TGANU | 5.1723 | 51071 | BBST132 132.00 | T3 | BBST132 | BBST132T3 | 20.2098 | BBST132 132.00 | T3 | BBST132 | BBST132T3 | 20.2098 | 51071 | DGUN132T2
[5 empty] | 75103 | T1 | 48.6 | DGUN132 | DGUN132T1 | TGANU | 5.2179 | 51071 | BBST132 132.00 | T4 | BBST132 | BBST132T4 | 20.1239 | BBST132 132.00 | T4 | BBST132 | BBST132T4 | 20.1239 | 51071 | DGUN132T1
[5 empty] | 75109 | T2 | 48.6 | CHRG132 | CHRG132T2 | TGANU | 14.3209 | 51037 | BBTC132 132.00 | T1 | BBTC132 | BBTC132T1 | 38.708 | BBTC132 132.00 | T1 | BBTC132 | BBTC132T1 | 38.708 | 51037 | CHRG132T2
[5 empty] | 75109 | T1 | 48.6 | CHRG132 | CHRG132T1 | TGANU | 17.8064 | 51037 | BBTC132 132.00 | T2 | BBTC132 | BBTC132T2 | 38.0753 | BBTC132 132.00 | T2 | BBTC132 | BBTC132T2 | 38.0753 | 51037 | CHRG132T1
[5 empty] | 97109 | T2 | 48.5 | KLUG132 | KLUG132T2 | JOHOR | 8.2529 | 51087 | BBTG132 132.00 | T1 | BBTG132 | BBTG132T1 | 6.3124 | BBTG132 132.00 | T1 | BBTG132 | BBTG132T1 | 6.3124 | 51087 | KLUG132T2
[5 empty] | 97109 | T1 | 48.5 | KLUG132 | KLUG132T1 | JOHOR | 8.5646 | 51087 | BBTG132 132.00 | T2 | BBTG132 | BBTG132T2 | 6.4698 | BBTG132 132.00 | T2 | BBTG132 | BBTG132T2 | 6.4698 | 51087 | KLUG132T1
[5 empty] | 97115 | T2 | 48.5 | MAJD132 | MAJD132T2 | JOHOR | 6.2513 | 51087 | BBTG132 132.00 | T3 | BBTG132 | BBTG132T3 | 20.0307 | BBTG132 132.00 | T3 | BBTG132 | BBTG132T3 | 20.0307 | 51087 | MAJD132T2
[5 empty] | 97115 | T1 | 48.5 | MAJD132 | MAJD132T1 | JOHOR | 6.5547 | 51087 | BBTG132 132.00 | T4 | BBTG132 | BBTG132T4 | 19.8681 | BBTG132 132.00 | T4 | BBTG132 | BBTG132T4 | 19.8681 | 51087 | MAJD132T1
[5 empty] | 75118 | T2 | 48.5 | DGID132 | DGID132T2 | TGANU | 25.8719 | 51078 | BCHG132 132.00 | T1 | BCHG132 | BCHG132T1 | 16.8289 | BCHG132 132.00 | T1 | BCHG132 | BCHG132T1 | 16.8289 | 51078 | DGID132T2
[5 empty] | 75118 | T1 | 48.5 | DGID132 | DGID132T1 | TGANU | 0 | 51078 | BCHG132 132.00 | T2 | BCHG132 | BCHG132T2 | 11.6928 | BCHG132 132.00 | T2 | BCHG132 | BCHG132T2 | 11.6928 | 51078 | DGID132T1
[5 empty] | 75144 | T2 | 48.5 | CKAI132 | CKAI132T2 | TGANU | 12.7594 | 51078 | BCHG132 132.00 | T3 | BCHG132 | BCHG132T3 | 26.4539 | BCHG132 132.00 | T3 | BCHG132 | BCHG132T3 | 26.4539 | 51078 | CKAI132T2
[5 empty] | 75144 | T1 | 48.5 | CKAI132 | CKAI132T1 | TGANU | 12.7325 | 51078 | BCHG132 132.00 | T4 | BCHG132 | BCHG132T4 | 26.1008 | BCHG132 132.00 | T4 | BCHG132 | BCHG132T4 | 26.1008 | 51078 | CKAI132T1
[5 empty] | 61132 | T4 | 48.5 | PAUH132 | PAUH132T4 | KEDAH | 10.8261 | 88194 | BCVS132 132.00 | T1 | BCVS132 | BCVS132T1 | 7.5726 | BCVS132 132.00 | T1 | BCVS132 | BCVS132T1 | 7.5726 | 88194 | PAUH132T4
[5 empty] | 61132 | T3 | 48.5 | PAUH132 | PAUH132T3 | KEDAH | 10.7723 | 88194 | BCVS132 132.00 | T2 | BCVS132 | BCVS132T2 | 11.0084 | BCVS132 132.00 | T2 | BCVS132 | BCVS132T2 | 11.0084 | 88194 | PAUH132T3
[5 empty] | 62108 | T4 | 48.5 | BMYK132 | BMYK132T4 | P PINANG | 48.2977 | 88194 | BCVS132 132.00 | T3 | BCVS132 | BCVS132T3 | 43.4019 | BCVS132 132.00 | T3 | BCVS132 | BCVS132T3 | 43.4019 | 88194 | BMYK132T4
[5 empty] | 62108 | T3 | 48.5 | BMYK132 | BMYK132T3 | P PINANG | 49.2069 | 88194 | BCVS132 132.00 | T4 | BCVS132 | BCVS132T4 | 43.8937 | BCVS132 132.00 | T4 | BCVS132 | BCVS132T4 | 43.8937 | 88194 | BMYK132T3
[5 empty] | 62108 | T2 | 48.5 | BMYK132 | BMYK132T2 | P PINANG | 14.6306 | 51060 | BHGT132 132.00 | T1 | BHGT132 | BHGT132T1 | 5.6238 | BHGT132 132.00 | T1 | BHGT132 | BHGT132T1 | 5.6238 | 51060 | BMYK132T2
[5 empty] | 62108 | T1 | 48.5 | BMYK132 | BMYK132T1 | P PINANG | 11.9517 | 51060 | BHGT132 132.00 | T2 | BHGT132 | BHGT132T2 | 9.627 | BHGT132 132.00 | T2 | BHGT132 | BHGT132T2 | 9.627 | 51060 | BMYK132T1
[5 empty] | 62155 | T4 | 48.5 | PRID132 | PRID132T4 | P PINANG | 36.9093 | 88177 | BJLL132 132.00 | T1 | BJLL132 | BJLL132T1 | 39.4245 | BJLL132 132.00 | T1 | BJLL132 | BJLL132T1 | 39.4245 | 88177 | PRID132T4
[5 empty] | 62155 | T3 | 48.5 | PRID132 | PRID132T3 | P PINANG | 36.8203 | 88177 | BJLL132 132.00 | T2 | BJLL132 | BJLL132T2 | 39.4804 | BJLL132 132.00 | T2 | BJLL132 | BJLL132T2 | 39.4804 | 88177 | PRID132T3
[5 empty] | 62155 | T2 | 48.5 | PRID132 | PRID132T2 | P PINANG | 23.4313 | 88177 | BJLL132 132.00 | T3 | BJLL132 | BJLL132T3 | 8.0168 | BJLL132 132.00 | T3 | BJLL132 | BJLL132T3 | 8.0168 | 88177 | PRID132T2
[5 empty] | 62155 | T1 | 48.5 | PRID132 | PRID132T1 | P PINANG | 23.6135 | 88177 | BJLL132 132.00 | T4 | BJLL132 | BJLL132T4 | 9.4023 | BJLL132 132.00 | T4 | BJLL132 | BJLL132T4 | 9.4023 | 88177 | PRID132T1
[5 empty] | 51103 | T3 | 48.5 | PCHP132 | PCHP132T3 | SELANGOR | 25.6452 | 51083 | BJTG132 132.00 | T1 | BJTG132 | BJTG132T1 | 8.1742 | BJTG132 132.00 | T1 | BJTG132 | BJTG132T1 | 8.1742 | 51083 | PCHP132T3
[5 empty] | 551103 | T2 | 48.5 | PCHP132 | PCHP132T2 | SELANGOR | 46.3707 | 51083 | BJTG132 132.00 | T2 | BJTG132 | BJTG132T2 | 5.6818 | BJTG132 132.00 | T2 | BJTG132 | BJTG132T2 | 5.6818 | 51083 | PCHP132T2
[5 empty] | 551103 | T1 | 48.5 | PCHP132 | PCHP132T1 | SELANGOR | 46.1988 | 51083 | BJTG132 132.00 | T3 | BJTG132 | BJTG132T3 | 35.82 | BJTG132 132.00 | T3 | BJTG132 | BJTG132T3 | 35.82 | 51083 | PCHP132T1
[5 empty] | 51006 | T4 | 48.5 | CBPS132 | CBPS132T4 | SELANGOR | 44.1744 | 51083 | BJTG132 132.00 | T4 | BJTG132 | BJTG132T4 | 35.1811 | BJTG132 132.00 | T4 | BJTG132 | BJTG132T4 | 35.1811 | 51083 | CBPS132T4
[5 empty] | 51006 | T3 | 48.5 | CBPS132 | CBPS132T3 | SELANGOR | 44.9676 | 51045 | BKPR132 132.00 | T1 | BKPR132 | BKPR132T1 | 14.6699 | BKPR132 132.00 | T1 | BKPR132 | BKPR132T1 | 14.6699 | 51045 | CBPS132T3
[5 empty] | 51027 | T2 | 48.5 | SHAB132 | SHAB132T2 | SELANGOR | 26.0252 | 51045 | BKPR132 132.00 | T2 | BKPR132 | BKPR132T2 | 16.307 | BKPR132 132.00 | T2 | BKPR132 | BKPR132T2 | 16.307 | 51045 | SHAB132T2
[5 empty] | 51027 | T1 | 48.5 | SHAB132 | SHAB132T1 | SELANGOR | 25.2341 | 51045 | BKPR132 132.00 | T3 | BKPR132 | BKPR132T3 | 38.7349 | BKPR132 132.00 | T3 | BKPR132 | BKPR132T3 | 38.7349 | 51045 | SHAB132T1
[5 empty] | 88122 | T2 | 48.5 | SGBT132 | SGBT132T2 | WPKL | 39.6472 | 51045 | BKPR132 132.00 | T4 | BKPR132 | BKPR132T4 | 38.7432 | BKPR132 132.00 | T4 | BKPR132 | BKPR132T4 | 38.7432 | 51045 | SGBT132T2
[5 empty] | 88122 | T1 | 48.5 | SGBT132 | SGBT132T1 | WPKL | 40.1111 | 51062 | BLKG132 132.00 | T1 | BLKG132 | BLKG132T1 | 8.6506 | BLKG132 132.00 | T1 | BLKG132 | BLKG132T1 | 8.6506 | 51062 | SGBT132T1
[5 empty] | 75206 | T2 | 48.5 | JELI275 | JELI275T2 | KELANTAN | 6.1705 | 51062 | BLKG132 132.00 | T2 | BLKG132 | BLKG132T2 | 5.0605 | BLKG132 132.00 | T2 | BLKG132 | BLKG132T2 | 5.0605 | 51062 | JELI275T2
[5 empty] | 75206 | T1 | 48.5 | JELI275 | JELI275T1 | KELANTAN | 6.3818 | 51062 | BLKG132 132.00 | T3 | BLKG132 | BLKG132T3 | 42.6936 | BLKG132 132.00 | T3 | BLKG132 | BLKG132T3 | 42.6936 | 51062 | JELI275T1
[5 empty] | 75114 | T2 | 48.5 | PPTH132 | PPTH132T2 | KELANTAN | 19.1226 | 51062 | BLKG132 132.00 | T4 | BLKG132 | BLKG132T4 | 41.9139 | BLKG132 132.00 | T4 | BLKG132 | BLKG132T4 | 41.9139 | 51062 | PPTH132T2
[5 empty] | 75114 | T1 | 48.5 | PPTH132 | PPTH132T1 | KELANTAN | 19.6103 | 51004 | BRGS132 132.00 | T1 | BRGS132 | BRGS132T1 | 8.0603 | BRGS132 132.00 | T1 | BRGS132 | BRGS132T1 | 8.0603 | 51004 | PPTH132T1
[5 empty] | 75106 | T5 | 48.5 | SJTH132 | SJTH132T5 | KELANTAN | 14.8915 | 51004 | BRGS132 132.00 | T2 | BRGS132 | BRGS132T2 | 10.8178 | BRGS132 132.00 | T2 | BRGS132 | BRGS132T2 | 10.8178 | 51004 | SJTH132T5
[5 empty] | 75106 | T2 | 48.5 | SJTH132 | SJTH132T2 | KELANTAN | 21.5291 | 51004 | BRGS132 132.00 | T3 | BRGS132 | BRGS132T3 | 0 | BRGS132 132.00 | T3 | BRGS132 | BRGS132T3 | 0 | 51004 | SJTH132T2
[5 empty] | 75106 | T1 | 48.5 | SJTH132 | SJTH132T1 | KELANTAN | 21.3261 | 51004 | BRGS132 132.00 | T4 | BRGS132 | BRGS132T4 | 0 | BRGS132 132.00 | T4 | BRGS132 | BRGS132T4 | 0 | 51004 | SJTH132T1
[5 empty] | 96195 | T2 | 48.4 | ZRNA132 | ZRNA132T2 | MELAKA | 6.7473 | 51053 | BRNG132 132.00 | T1 | BRNG132 | BRNG132T1 | 0 | BRNG132 132.00 | T1 | BRNG132 | BRNG132T1 | 0 | 51053 | ZRNA132T2
[5 empty] | 96195 | T1 | 48.4 | ZRNA132 | ZRNA132T1 | MELAKA | 6.7297 | 51053 | BRNG132 132.00 | T2 | BRNG132 | BRNG132T2 | 19.6879 | BRNG132 132.00 | T2 | BRNG132 | BRNG132T2 | 19.6879 | 51053 | ZRNA132T1
[5 empty] | 96181 | F3 | 48.4 | SPWR132 | SPWR132F3 | MELAKA | 3.321 | 51053 | BRNG132 132.00 | T3 | BRNG132 | BRNG132T3 | 0 | BRNG132 132.00 | T3 | BRNG132 | BRNG132T3 | 0 | 51053 | SPWR132F3
[5 empty] | 96181 | F2 | 48.4 | SPWR132 | SPWR132F2 | MELAKA | 2.321 | 51053 | BRNG132 132.00 | T4 | BRNG132 | BRNG132T4 | 0 | BRNG132 132.00 | T4 | BRNG132 | BRNG132T4 | 0 | 51053 | SPWR132F2
[5 empty] | 96181 | F1 | 48.4 | SPWR132 | SPWR132F1 | MELAKA | 1.321 | 51056 | BSTA132 132.00 | T1 | BSTA132 | BSTA132T1 | 6.1623 | BSTA132 132.00 | T1 | BSTA132 | BSTA132T1 | 6.1623 | 51056 | SPWR132F1
[5 empty] | 96191 | T4 | 48.4 | CHNG132 | CHNG132T4 | MELAKA | 31.8509 | 51056 | BSTA132 132.00 | T2 | BSTA132 | BSTA132T2 | 11.1047 | BSTA132 132.00 | T2 | BSTA132 | BSTA132T2 | 11.1047 | 51056 | CHNG132T4
[5 empty] | 96191 | T3 | 48.4 | CHNG132 | CHNG132T3 | MELAKA | 31.8406 | 51056 | BSTA132 132.00 | T3 | BSTA132 | BSTA132T3 | 15.17 | BSTA132 132.00 | T3 | BSTA132 | BSTA132T3 | 15.17 | 51056 | CHNG132T3
[5 empty] | 96191 | T2 | 48.4 | CHNG132 | CHNG132T2 | MELAKA | 10.6045 | 51056 | BSTA132 132.00 | T4 | BSTA132 | BSTA132T4 | 15.227 | BSTA132 132.00 | T4 | BSTA132 | BSTA132T4 | 15.227 | 51056 | CHNG132T2
[5 empty] | 96191 | T1 | 48.4 | CHNG132 | CHNG132T1 | MELAKA | 7.3438 | 51001 | BTAI132 132.00 | T1 | BTAI132 | BTAI132T1 | 11.8761 | BTAI132 132.00 | T1 | BTAI132 | BTAI132T1 | 11.8761 | 51001 | CHNG132T1
[5 empty] | 96111 | T2 | 48.4 | BMKA132 | BMKA132T2 | MELAKA | 8.8483 | 51001 | BTAI132 132.00 | T2 | BTAI132 | BTAI132T2 | 0 | BTAI132 132.00 | T2 | BTAI132 | BTAI132T2 | 0 | 51001 | BMKA132T2
[5 empty] | 96111 | T1 | 48.4 | BMKA132 | BMKA132T1 | MELAKA | 5.6828 | 51048 | BTGA132 132.00 | T1 | BTGA132 | BTGA132T1 | 18.814 | BTGA132 132.00 | T1 | BTGA132 | BTGA132T1 | 18.814 | 51048 | BMKA132T1
[5 empty] | 96108 | T2 | 48.4 | MMKA132 | MMKA132T2 | MELAKA | 7.0093 | 51048 | BTGA132 132.00 | T2 | BTGA132 | BTGA132T2 | 19.0863 | BTGA132 132.00 | T2 | BTGA132 | BTGA132T2 | 19.0863 | 51048 | MMKA132T2
[5 empty] | 96108 | T1 | 48.4 | MMKA132 | MMKA132T1 | MELAKA | 9.3723 | 51048 | BTGA132 132.00 | T3 | BTGA132 | BTGA132T3 | 0 | BTGA132 132.00 | T3 | BTGA132 | BTGA132T3 | 0 | 51048 | MMKA132T1
[5 empty] | 96122 | T2 | 48.4 | BVTA132 | BVTA132T2 | MELAKA | 8.5501 | 151088 | BTIC-T 132.00 | T7 | BTIC-T | BTIC-T T7 | 0 | BTIC-T 132.00 | T7 | BTIC-T | BTIC-T T7 | 0 | 151088 | BVTA132T2
[5 empty] | 96122 | T1 | 48.4 | BVTA132 | BVTA132T1 | MELAKA | 3.3695 | 51088 | BTIC132 132.00 | T7 | BTIC132 | BTIC132T7 | 0 | BTIC132 132.00 | T7 | BTIC132 | BTIC132T7 | 0 | 51088 | BVTA132T1
[5 empty] | 96189 | T4 | 48.4 | TGBU132 | TGBU132T4 | MELAKA | 16.861 | 51008 | BTIN132 132.00 | T1 | BTIN132 | BTIN132T1 | 52.4149 | BTIN132 132.00 | T1 | BTIN132 | BTIN132T1 | 52.4149 | 51008 | TGBU132T4
[5 empty] | 96189 | T3 | 48.4 | TGBU132 | TGBU132T3 | MELAKA | 16.7823 | 51008 | BTIN132 132.00 | T2 | BTIN132 | BTIN132T2 | 54.3067 | BTIN132 132.00 | T2 | BTIN132 | BTIN132T2 | 54.3067 | 51008 | TGBU132T3
[5 empty] | 96189 | T2 | 48.4 | TGBU132 | TGBU132T2 | MELAKA | 3.6387 | 51112 | CBJN132 132.00 | T1 | CBJN132 | CBJN132T1 | 5.4633 | CBJN132 132.00 | T1 | CBJN132 | CBJN132T1 | 5.4633 | 51112 | TGBU132T2
[5 empty] | 96189 | T1 | 48.4 | TGBU132 | TGBU132T1 | MELAKA | 3.7268 | 51112 | CBJN132 132.00 | T2 | CBJN132 | CBJN132T2 | 6.2637 | CBJN132 132.00 | T2 | CBJN132 | CBJN132T2 | 6.2637 | 51112 | TGBU132T1
[5 empty] | 96197 | F2 | 48.4 | PPSR132 | PPSR132F2 | MELAKA | 0.1243 | 51112 | CBJN132 132.00 | T3 | CBJN132 | CBJN132T3 | 29.5593 | CBJN132 132.00 | T3 | CBJN132 | CBJN132T3 | 29.5593 | 51112 | PPSR132F2
[5 empty] | 96197 | F1 | 48.4 | PPSR132 | PPSR132F1 | MELAKA | 2.7441 | 51112 | CBJN132 132.00 | T4 | CBJN132 | CBJN132T4 | 29.7043 | CBJN132 132.00 | T4 | CBJN132 | CBJN132T4 | 29.7043 | 51112 | PPSR132F1
[5 empty] | 96196 | F1 | 48.4 | HLNM132 | HLNM132F1 | MELAKA | 9.539 | 51006 | CBPS132 132.00 | T1 | CBPS132 | CBPS132T1 | 15.869 | CBPS132 132.00 | T1 | CBPS132 | CBPS132T1 | 15.869 | 51006 | HLNM132F1
[5 empty] | 96101 | T4 | 48.4 | BRBI132 | BRBI132T4 | MELAKA | 10.1313 | 51006 | CBPS132 132.00 | T2 | CBPS132 | CBPS132T2 | 12.0988 | CBPS132 132.00 | T2 | CBPS132 | CBPS132T2 | 12.0988 | 51006 | BRBI132T4
[5 empty] | 96101 | T3 | 48.4 | BRBI132 | BRBI132T3 | MELAKA | 10.1531 | 51006 | CBPS132 132.00 | T3 | CBPS132 | CBPS132T3 | 44.9676 | CBPS132 132.00 | T3 | CBPS132 | CBPS132T3 | 44.9676 | 51006 | BRBI132T3
[5 empty] | 96101 | T2 | 48.4 | BRBI132 | BRBI132T2 | MELAKA | 9.1227 | 51006 | CBPS132 132.00 | T4 | CBPS132 | CBPS132T4 | 44.1744 | CBPS132 132.00 | T4 | CBPS132 | CBPS132T4 | 44.1744 | 51006 | BRBI132T2
[5 empty] | 96101 | T1 | 48.4 | BRBI132 | BRBI132T1 | MELAKA | 6.6624 | 51038 | CJYA132 132.00 | T1 | CJYA132 | CJYA132T1 | 31.8343 | CJYA132 132.00 | T1 | CJYA132 | CJYA132T1 | 31.8343 | 51038 | BRBI132T1
[5 empty] | 75116 | T4 | 48.4 | GBDK132 | GBDK132T4 | TGANU | 19.4291 | 51038 | CJYA132 132.00 | T2 | CJYA132 | CJYA132T2 | 33.5056 | CJYA132 132.00 | T2 | CJYA132 | CJYA132T2 | 33.5056 | 51038 | GBDK132T4
[5 empty] | 75116 | T3 | 48.4 | GBDK132 | GBDK132T3 | TGANU | 19.3752 | 51038 | CJYA132 132.00 | T3 | CJYA132 | CJYA132T3 | 66.9274 | CJYA132 132.00 | T3 | CJYA132 | CJYA132T3 | 66.9274 | 51038 | GBDK132T3
[5 empty] | 75116 | T2 | 48.4 | GBDK132 | GBDK132T2 | TGANU | 10.6832 | 52008 | EGDC275 275.00 | T1 | EGDC275 | EGDC275T1 | 2.129 | EGDC275 275.00 | T1 | EGDC275 | EGDC275T1 | 2.129 | 52008 | GBDK132T2
[5 empty] | 75116 | T1 | 48.4 | GBDK132 | GBDK132T1 | TGANU | 10.6625 | 51067 | ELMW132 132.00 | T1 | ELMW132 | ELMW132T1 | 0 | ELMW132 132.00 | T1 | ELMW132 | ELMW132T1 | 0 | 51067 | GBDK132T1
[5 empty] | 75140 | T4 | 48.4 | KBRG132 | KBRG132T4 | TGANU | 5.133 | 51067 | ELMW132 132.00 | T2 | ELMW132 | ELMW132T2 | 0 | ELMW132 132.00 | T2 | ELMW132 | ELMW132T2 | 0 | 51067 | KBRG132T4
[5 empty] | 75140 | T3 | 48.4 | KBRG132 | KBRG132T3 | TGANU | 5.0563 | 96169 | ESTK132 132.00 | T1 | ESTK132 | ESTK132T1 | 22.637 | ESTK132 132.00 | T1 | ESTK132 | ESTK132T1 | 22.637 | 96169 | KBRG132T3
[5 empty] | 75140 | T2 | 48.4 | KBRG132 | KBRG132T2 | TGANU | 10.4865 | 96169 | ESTK132 132.00 | T2 | ESTK132 | ESTK132T2 | 22.8441 | ESTK132 132.00 | T2 | ESTK132 | ESTK132T2 | 22.8441 | 96169 | KBRG132T2
[5 empty] | 75140 | T1 | 48.4 | KBRG132 | KBRG132T1 | TGANU | 10.8862 | 51072 | HCOM132 132.00 | T1 | HCOM132 | HCOM132T1 | 38.7888 | HCOM132 132.00 | T1 | HCOM132 | HCOM132T1 | 38.7888 | 51072 | KBRG132T1
[5 empty] | 75115 | T4 | 48.4 | KTGU132 | KTGU132T4 | TGANU | 11.5365 | 51072 | HCOM132 132.00 | T2 | HCOM132 | HCOM132T2 | 34.0078 | HCOM132 132.00 | T2 | HCOM132 | HCOM132T2 | 34.0078 | 51072 | KTGU132T4
[5 empty] | 75115 | T3 | 48.4 | KTGU132 | KTGU132T3 | TGANU | 11.521 | 51072 | HCOM132 132.00 | T3 | HCOM132 | HCOM132T3 | 6.7442 | HCOM132 132.00 | T3 | HCOM132 | HCOM132T3 | 6.7442 | 51072 | KTGU132T3
[5 empty] | 75115 | T2 | 48.4 | KTGU132 | KTGU132T2 | TGANU | 11.4909 | 51072 | HCOM132 132.00 | T4 | HCOM132 | HCOM132T4 | 9.6643 | HCOM132 132.00 | T4 | HCOM132 | HCOM132T4 | 9.6643 | 51072 | KTGU132T2
[5 empty] | 75115 | T1 | 48.4 | KTGU132 | KTGU132T1 | TGANU | 13.361 | 51047 | IGBK132 132.00 | T1 | IGBK132 | IGBK132T1 | 10.7733 | IGBK132 132.00 | T1 | IGBK132 | IGBK132T1 | 10.7733 | 51047 | KTGU132T1
[5 empty] | 75138 | T3 | 48.4 | BRKT132 | BRKT132T3 | TGANU | 14.7041 | 51047 | IGBK132 132.00 | T2 | IGBK132 | IGBK132T2 | 11.6069 | IGBK132 132.00 | T2 | IGBK132 | IGBK132T2 | 11.6069 | 51047 | BRKT132T3
[5 empty] | 75138 | T2 | 48.4 | BRKT132 | BRKT132T2 | TGANU | 9.0182 | 51047 | IGBK132 132.00 | T3 | IGBK132 | IGBK132T3 | 20.9937 | IGBK132 132.00 | T3 | IGBK132 | IGBK132T3 | 20.9937 | 51047 | BRKT132T2
[5 empty] | 75138 | T1 | 48.4 | BRKT132 | BRKT132T1 | TGANU | 9.1207 | 51047 | IGBK132 132.00 | T4 | IGBK132 | IGBK132T4 | 19.282 | IGBK132 132.00 | T4 | IGBK132 | IGBK132T4 | 19.282 | 51047 | BRKT132T1
[5 empty] | 97143 | T4 | 48.4 | SLNG132 | SLNG132T4 | JOHOR | 29.0064 | 51031 | KCPK132 132.00 | T1 | KCPK132 | KCPK132T1 | 31.1292 | KCPK132 132.00 | T1 | KCPK132 | KCPK132T1 | 31.1292 | 51031 | SLNG132T4
[5 empty] | 97143 | T3 | 48.4 | SLNG132 | SLNG132T3 | JOHOR | 29.1514 | 51031 | KCPK132 132.00 | T2 | KCPK132 | KCPK132T2 | 31.0246 | KCPK132 132.00 | T2 | KCPK132 | KCPK132T2 | 31.0246 | 51031 | SLNG132T3
[5 empty] | 97143 | T2 | 48.4 | SLNG132 | SLNG132T2 | JOHOR | 13.5661 | 51011 | KDSA132 132.00 | T1 | KDSA132 | KDSA132T1 | 8.5201 | KDSA132 132.00 | T1 | KDSA132 | KDSA132T1 | 8.5201 | 51011 | SLNG132T2
[5 empty] | 97143 | T1 | 48.4 | SLNG132 | SLNG132T1 | JOHOR | 12.4767 | 51011 | KDSA132 132.00 | T2 | KDSA132 | KDSA132T2 | 10.7361 | KDSA132 132.00 | T2 | KDSA132 | KDSA132T2 | 10.7361 | 51011 | SLNG132T1
[5 empty] | 97162 | T4 | 48.4 | SNAI132 | SNAI132T4 | JOHOR | 42.6719 | 51011 | KDSA132 132.00 | T3 | KDSA132 | KDSA132T3 | 51.0346 | KDSA132 132.00 | T3 | KDSA132 | KDSA132T3 | 51.0346 | 51011 | SNAI132T4
[5 empty] | 97162 | T3 | 48.4 | SNAI132 | SNAI132T3 | JOHOR | 43.0695 | 51011 | KDSA132 132.00 | T4 | KDSA132 | KDSA132T4 | 39.992 | KDSA132 132.00 | T4 | KDSA132 | KDSA132T4 | 39.992 | 51011 | SNAI132T3
[5 empty] | 97162 | T2 | 48.4 | SNAI132 | SNAI132T2 | JOHOR | 9.6229 | 51011 | KDSA132 132.00 | T5 | KDSA132 | KDSA132T5 | 40.8152 | KDSA132 132.00 | T5 | KDSA132 | KDSA132T5 | 40.8152 | 51011 | SNAI132T2
[5 empty] | 97162 | T1 | 48.4 | SNAI132 | SNAI132T1 | JOHOR | 9.6219 | 51055 | KJNG132 132.00 | T1 | KJNG132 | KJNG132T1 | 12.6559 | KJNG132 132.00 | T1 | KJNG132 | KJNG132T1 | 12.6559 | 51055 | SNAI132T1
[5 empty] | 97112 | T1 | 48.4 | KLAI132 | KLAI132T1 | JOHOR | 0 | 51055 | KJNG132 132.00 | T2 | KJNG132 | KJNG132T2 | 15.4838 | KJNG132 132.00 | T2 | KJNG132 | KJNG132T2 | 15.4838 | 51055 | KLAI132T1
[5 empty] | 597112 | T2 | 48.4 | KLAI132R | KLAI132RT2 | JOHOR | 20.1353 | 51055 | KJNG132 132.00 | T3 | KJNG132 | KJNG132T3 | 39.6617 | KJNG132 132.00 | T3 | KJNG132 | KJNG132T3 | 39.6617 | 51055 | KLAI132RT2
[5 empty] | 97159 | F1 | 48.4 | UTMJ132 | UTMJ132F1 | JOHOR | 4.0799 | 51055 | KJNG132 132.00 | T4 | KJNG132 | KJNG132T4 | 39.787 | KJNG132 132.00 | T4 | KJNG132 | KJNG132T4 | 39.787 | 51055 | UTMJ132F1
[5 empty] | 597159 | F2 | 48.4 | UTMJ132R | UTMJ132RF2 | JOHOR | 1.3565 | 51036 | KKMG132 132.00 | T1 | KKMG132 | KKMG132T1 | 6.8622 | KKMG132 132.00 | T1 | KKMG132 | KKMG132T1 | 6.8622 | 51036 | UTMJ132RF2
[5 empty] | 51001 | T2 | 48.4 | BTAI132 | BTAI132T2 | SELANGOR | 0 | 51036 | KKMG132 132.00 | T2 | KKMG132 | KKMG132T2 | 7.7538 | KKMG132 132.00 | T2 | KKMG132 | KKMG132T2 | 7.7538 | 51036 | BTAI132T2
[5 empty] | 51001 | T1 | 48.4 | BTAI132 | BTAI132T1 | SELANGOR | 11.8761 | 51036 | KKMG132 132.00 | T3 | KKMG132 | KKMG132T3 | 44.4291 | KKMG132 132.00 | T3 | KKMG132 | KKMG132T3 | 44.4291 | 51036 | BTAI132T1
[5 empty] | 588124 | T2 | 48.4 | KULE132 | KULE132T2 | WPKL | 39.3707 | 51036 | KKMG132 132.00 | T4 | KKMG132 | KKMG132T4 | 45.1436 | KKMG132 132.00 | T4 | KKMG132 | KKMG132T4 | 45.1436 | 51036 | KULE132T2
[5 empty] | 588124 | T1 | 48.4 | KULE132 | KULE132T1 | WPKL | 39.3697 | 51018 | KLIA132 132.00 | T1 | KLIA132 | KLIA132T1 | 6.2534 | KLIA132 132.00 | T1 | KLIA132 | KLIA132T1 | 6.2534 | 51018 | KULE132T1
[5 empty] | 88163 | T2 | 48.4 | KLPV132 | KLPV132T2 | WPKL | 28.6108 | 51018 | KLIA132 132.00 | T2 | KLIA132 | KLIA132T2 | 4.9652 | KLIA132 132.00 | T2 | KLIA132 | KLIA132T2 | 4.9652 | 51018 | KLPV132T2
[5 empty] | 88163 | T1 | 48.4 | KLPV132 | KLPV132T1 | WPKL | 28.5694 | 51018 | KLIA132 132.00 | T3 | KLIA132 | KLIA132T3 | 62.8278 | KLIA132 132.00 | T3 | KLIA132 | KLIA132T3 | 62.8278 | 51018 | KLPV132T1
[5 empty] | 61112 | T2 | 48.4 | TKBU132 | TKBU132T2 | KEDAH | 31.707 | 51018 | KLIA132 132.00 | T4 | KLIA132 | KLIA132T4 | 0 | KLIA132 132.00 | T4 | KLIA132 | KLIA132T4 | 0 | 51018 | TKBU132T2
[5 empty] | 61112 | T1 | 48.4 | TKBU132 | TKBU132T1 | KEDAH | 31.6376 | 52020 | KLPP275 275.00 | T1 | KLPP275 | KLPP275T1 | 0 | KLPP275 275.00 | T1 | KLPP275 | KLPP275T1 | 0 | 52020 | TKBU132T1
[5 empty] | #N/A | T3 | 48.3 | TPOI132 | TPOI132T3 | #N/A | #N/A | 52020 | KLPP275 275.00 | T2 | KLPP275 | KLPP275T2 | 0 | KLPP275 275.00 | T2 | KLPP275 | KLPP275T2 | 0 | 52020 | TPOI132T3
[5 empty] | 97127 | T2 | 48.3 | TPOI132 | TPOI132T2 | JOHOR | 11.9165 | 52020 | KLPP275 275.00 | T3 | KLPP275 | KLPP275T3 | 0 | KLPP275 275.00 | T3 | KLPP275 | KLPP275T3 | 0 | 52020 | TPOI132T2
[5 empty] | 97127 | T1 | 48.3 | TPOI132 | TPOI132T1 | JOHOR | 11.9093 | 51026 | KPNG132 132.00 | T1 | KPNG132 | KPNG132T1 | 6.5754 | KPNG132 132.00 | T1 | KPNG132 | KPNG132T1 | 6.5754 | 51026 | TPOI132T1
[5 empty] | 97129 | T2 | 48.3 | BPHT132 | BPHT132T2 | JOHOR | 11.8906 | 51026 | KPNG132 132.00 | T2 | KPNG132 | KPNG132T2 | 6.5806 | KPNG132 132.00 | T2 | KPNG132 | KPNG132T2 | 6.5806 | 51026 | BPHT132T2
[5 empty] | 97129 | T1 | 48.3 | BPHT132 | BPHT132T1 | JOHOR | 11.055 | 51014 | KSBG132 132.00 | T1 | KSBG132 | KSBG132T1 | 12.5554 | KSBG132 132.00 | T1 | KSBG132 | KSBG132T1 | 12.5554 | 51014 | BPHT132T1
[5 empty] | 97121 | T2 | 48.3 | TPCH132 | TPCH132T2 | JOHOR | 4.8668 | 51014 | KSBG132 132.00 | T2 | KSBG132 | KSBG132T2 | 6.2368 | KSBG132 132.00 | T2 | KSBG132 | KSBG132T2 | 6.2368 | 51014 | TPCH132T2
[5 empty] | 97121 | T1 | 48.3 | TPCH132 | TPCH132T1 | JOHOR | 11.4329 | 51014 | KSBG132 132.00 | T3 | KSBG132 | KSBG132T3 | 25.9776 | KSBG132 132.00 | T3 | KSBG132 | KSBG132T3 | 25.9776 | 51014 | TPCH132T1
[5 empty] | 97107 | T2 | 48.3 | YGPG132 | YGPG132T2 | JOHOR | 9.8683 | 51014 | KSBG132 132.00 | T4 | KSBG132 | KSBG132T4 | 25.8895 | KSBG132 132.00 | T4 | KSBG132 | KSBG132T4 | 25.8895 | 51014 | YGPG132T2
[5 empty] | 97107 | T1 | 48.3 | YGPG132 | YGPG132T1 | JOHOR | 11.4443 | 51016 | KSGR132 132.00 | T1 | KSGR132 | KSGR132T1 | 30.9656 | KSGR132 132.00 | T1 | KSGR132 | KSGR132T1 | 30.9656 | 51016 | YGPG132T1
[5 empty] | 51057 | T4 | 48.3 | MERU132 | MERU132T4 | SELANGOR | 44.0532 | 51016 | KSGR132 132.00 | T2 | KSGR132 | KSGR132T2 | 31.2338 | KSGR132 132.00 | T2 | KSGR132 | KSGR132T2 | 31.2338 | 51016 | MERU132T4
[5 empty] | 51057 | T3 | 48.3 | MERU132 | MERU132T3 | SELANGOR | 43.9352 | 51069 | LGMR132 132.00 | F1 | LGMR132 | LGMR132F1 | 1.7945 | LGMR132 132.00 | F1 | LGMR132 | LGMR132F1 | 1.7945 | 51069 | MERU132T3
[5 empty] | 51009 | T3 | 48.3 | PROT132 | PROT132T3 | SELANGOR | 49.7164 | 51069 | LGMR132 132.00 | F2 | LGMR132 | LGMR132F2 | 1.5419 | LGMR132 132.00 | F2 | LGMR132 | LGMR132F2 | 1.5419 | 51069 | PROT132T3
[5 empty] | 51009 | T2 | 48.3 | PROT132 | PROT132T2 | SELANGOR | 32.2796 | 51085 | LKDG132 132.00 | T1 | LKDG132 | LKDG132T1 | 11.2134 | LKDG132 132.00 | T1 | LKDG132 | LKDG132T1 | 11.2134 | 51085 | PROT132T2
[5 empty] | 51009 | T1 | 48.3 | PROT132 | PROT132T1 | SELANGOR | 32.4039 | 51085 | LKDG132 132.00 | T2 | LKDG132 | LKDG132T2 | 12.1588 | LKDG132 132.00 | T2 | LKDG132 | LKDG132T2 | 12.1588 | 51085 | PROT132T1
[5 empty] | 96132 | T2 | 48.3 | KLAT132 | KLAT132T2 | NS | 9.5856 | 51085 | LKDG132 132.00 | T3 | LKDG132 | LKDG132T3 | 28.645 | LKDG132 132.00 | T3 | LKDG132 | LKDG132T3 | 28.645 | 51085 | KLAT132T2
[5 empty] | 96132 | T1 | 48.3 | KLAT132 | KLAT132T1 | NS | 13.7411 | 51085 | LKDG132 132.00 | T4 | LKDG132 | LKDG132T4 | 28.47 | LKDG132 132.00 | T4 | LKDG132 | LKDG132T4 | 28.47 | 51085 | KLAT132T1
[5 empty] | 61103 | T2 | 48.3 | TEWA132 | TEWA132T2 | LANGKAWI | 33.2882 | 51058 | LSHA132 132.00 | T1 | LSHA132 | LSHA132T1 | 1.5398 | LSHA132 132.00 | T1 | LSHA132 | LSHA132T1 | 1.5398 | 51058 | TEWA132T2
[5 empty] | 61103 | T1 | 48.3 | TEWA132 | TEWA132T1 | LANGKAWI | 0 | 51058 | LSHA132 132.00 | T2 | LSHA132 | LSHA132T2 | 0 | LSHA132 132.00 | T2 | LSHA132 | LSHA132T2 | 0 | 51058 | TEWA132T1
[5 empty] | 61125 | T4 | 48.3 | UMKA132 | UMKA132T4 | LANGKAWI | 17.1541 | 51057 | MERU132 132.00 | T1 | MERU132 | MERU132T1 | 8.6112 | MERU132 132.00 | T1 | MERU132 | MERU132T1 | 8.6112 | 51057 | UMKA132T4
[5 empty] | 61125 | T3 | 48.3 | UMKA132 | UMKA132T3 | LANGKAWI | 17.299 | 51057 | MERU132 132.00 | T2 | MERU132 | MERU132T2 | 11.4267 | MERU132 132.00 | T2 | MERU132 | MERU132T2 | 11.4267 | 51057 | UMKA132T3
[5 empty] | 61125 | T2 | 48.3 | UMKA132 | UMKA132T2 | LANGKAWI | 3.7237 | 51057 | MERU132 132.00 | T3 | MERU132 | MERU132T3 | 43.9352 | MERU132 132.00 | T3 | MERU132 | MERU132T3 | 43.9352 | 51057 | UMKA132T2
[5 empty] | 61125 | T1 | 48.3 | UMKA132 | UMKA132T1 | LANGKAWI | 3.7268 | 51057 | MERU132 132.00 | T4 | MERU132 | MERU132T4 | 44.0532 | MERU132 132.00 | T4 | MERU132 | MERU132T4 | 44.0532 | 51057 | UMKA132T1
[5 empty] | 561145 | F2 | 48.3 | KCMT132R | KCMT132RF2 | LANGKAWI | 26.1764 | 51022 | MHTA132 132.00 | T1 | MHTA132 | MHTA132T1 | 7.6782 | MHTA132 132.00 | T1 | MHTA132 | MHTA132T1 | 7.6782 | 51022 | KCMT132RF2
[5 empty] | 61145 | F1 | 48.3 | KCMT132 | KCMT132F1 | LANGKAWI | 0 | 51022 | MHTA132 132.00 | T2 | MHTA132 | MHTA132T2 | 5.6807 | MHTA132 132.00 | T2 | MHTA132 | MHTA132T2 | 5.6807 | 51022 | KCMT132F1
[5 empty] | 88161 | T5 | 48.3 | IMBI132 | IMBI132T5 | WPKL | 33.9478 | 51022 | MHTA132 132.00 | T3 | MHTA132 | MHTA132T3 | 31.2596 | MHTA132 132.00 | T3 | MHTA132 | MHTA132T3 | 31.2596 | 51022 | IMBI132T5
[5 empty] | 88161 | T4 | 48.3 | IMBI132 | IMBI132T4 | WPKL | 25.6182 | 51022 | MHTA132 132.00 | T4 | MHTA132 | MHTA132T4 | 31.3373 | MHTA132 132.00 | T4 | MHTA132 | MHTA132T4 | 31.3373 | 51022 | IMBI132T4
[5 empty] | 88161 | T3 | 48.3 | IMBI132 | IMBI132T3 | WPKL | 25.4443 | 51005 | NKST132 132.00 | T3 | NKST132 | NKST132T3 | 29.2062 | NKST132 132.00 | T3 | NKST132 | NKST132T3 | 29.2062 | 51005 | IMBI132T3
[5 empty] | 51011 | T5 | 48.3 | KDSA132 | KDSA132T5 | SELANGOR | 40.8152 | 51005 | NKST132 132.00 | T4 | NKST132 | NKST132T4 | 29.3491 | NKST132 132.00 | T4 | NKST132 | NKST132T4 | 29.3491 | 51005 | KDSA132T5
[5 empty] | 51011 | T4 | 48.3 | KDSA132 | KDSA132T4 | SELANGOR | 39.992 | 51200 | NRWG132 132.00 | T1 | NRWG132 | NRWG132T1 | 37.6476 | NRWG132 132.00 | T1 | NRWG132 | NRWG132T1 | 37.6476 | 51200 | KDSA132T4
[5 empty] | 51011 | T3 | 48.3 | KDSA132 | KDSA132T3 | SELANGOR | 51.0346 | 51200 | NRWG132 132.00 | T2 | NRWG132 | NRWG132T2 | 37.5762 | NRWG132 132.00 | T2 | NRWG132 | NRWG132T2 | 37.5762 | 51200 | KDSA132T3
[5 empty] | 88133 | T2 | 48.3 | GWAY132 | GWAY132T2 | WPKL | 13.302 | 51200 | NRWG132 132.00 | T3 | NRWG132 | NRWG132T3 | 12.9852 | NRWG132 132.00 | T3 | NRWG132 | NRWG132T3 | 12.9852 | 51200 | GWAY132T2
[5 empty] | 88133 | T1 | 48.3 | GWAY132 | GWAY132T1 | WPKL | 13.3186 | 51200 | NRWG132 132.00 | T4 | NRWG132 | NRWG132T4 | 6.6593 | NRWG132 132.00 | T4 | NRWG132 | NRWG132T4 | 6.6593 | 51200 | GWAY132T1
[5 empty] | 62126 | F2 | 48.3 | JNKO132 | JNKO132F2 | P PINANG | 0.0332 | 51025 | NSDA132 132.00 | T1 | NSDA132 | NSDA132T1 | 31.0536 | NSDA132 132.00 | T1 | NSDA132 | NSDA132T1 | 31.0536 | 51025 | JNKO132F2
[5 empty] | 62126 | F1 | 48.3 | JNKO132 | JNKO132F1 | P PINANG | 0.3334 | 51025 | NSDA132 132.00 | T2 | NSDA132 | NSDA132T2 | 31.0919 | NSDA132 132.00 | T2 | NSDA132 | NSDA132T2 | 31.0919 | 51025 | JNKO132F1
[5 empty] | 62122 | T2 | 48.3 | VDOR132 | VDOR132T2 | P PINANG | 15.5097 | 51025 | NSDA132 132.00 | T3 | NSDA132 | NSDA132T3 | 4.6784 | NSDA132 132.00 | T3 | NSDA132 | NSDA132T3 | 4.6784 | 51025 | VDOR132T2
[5 empty] | 62122 | T1 | 48.3 | VDOR132 | VDOR132T1 | P PINANG | 12.69 | 51025 | NSDA132 132.00 | T4 | NSDA132 | NSDA132T4 | 6.0059 | NSDA132 132.00 | T4 | NSDA132 | NSDA132T4 | 6.0059 | 51025 | VDOR132T1
[5 empty] | 63118 | T2 | 48.3 | PBTR132 | PBTR132T2 | PERAK | 22.1845 | 51091 | NSPK132 132.00 | T1 | NSPK132 | NSPK132T1 | 26.3079 | NSPK132 132.00 | T1 | NSPK132 | NSPK132T1 | 26.3079 | 51091 | PBTR132T2
[5 empty] | 63118 | T1 | 48.3 | PBTR132 | PBTR132T1 | PERAK | 19.1557 | 51091 | NSPK132 132.00 | T2 | NSPK132 | NSPK132T2 | 25.7756 | NSPK132 132.00 | T2 | NSPK132 | NSPK132T2 | 25.7756 | 51091 | PBTR132T1
[5 empty] | 62111 | T2 | 48.3 | NTBL132 | NTBL132T2 | P PINANG | 14.8252 | 51091 | NSPK132 132.00 | T3 | NSPK132 | NSPK132T3 | 6.8012 | NSPK132 132.00 | T3 | NSPK132 | NSPK132T3 | 6.8012 | 51091 | NTBL132T2
[5 empty] | 62111 | T1 | 48.3 | NTBL132 | NTBL132T1 | P PINANG | 11.9238 | 51091 | NSPK132 132.00 | T4 | NSPK132 | NSPK132T4 | 6.1778 | NSPK132 132.00 | T4 | NSPK132 | NSPK132T4 | 6.1778 | 51091 | NTBL132T1
[5 empty] | 62135 | T2 | 48.2 | SPNG132 | SPNG132T2 | P PINANG | 25.9372 | 51023 | NUNI132 132.00 | T1 | NUNI132 | NUNI132T1 | 12.719 | NUNI132 132.00 | T1 | NUNI132 | NUNI132T1 | 12.719 | 51023 | SPNG132T2
[5 empty] | 62135 | T1 | 48.2 | SPNG132 | SPNG132T1 | P PINANG | 27.4583 | 51023 | NUNI132 132.00 | T2 | NUNI132 | NUNI132T2 | 13.096 | NUNI132 132.00 | T2 | NUNI132 | NUNI132T2 | 13.096 | 51023 | SPNG132T1
[5 empty] | 51060 | T2 | 48.2 | BHGT132 | BHGT132T2 | SELANGOR | 9.627 | 51023 | NUNI132 132.00 | T3 | NUNI132 | NUNI132T3 | 34.1166 | NUNI132 132.00 | T3 | NUNI132 | NUNI132T3 | 34.1166 | 51023 | BHGT132T2
[5 empty] | 51060 | T1 | 48.2 | BHGT132 | BHGT132T1 | SELANGOR | 5.6238 | 51023 | NUNI132 132.00 | T4 | NUNI132 | NUNI132T4 | 34.8124 | NUNI132 132.00 | T4 | NUNI132 | NUNI132T4 | 34.8124 | 51023 | BHGT132T1
[5 empty] | 96152 | T4 | 48.2 | AMID132 | AMID132T4 | NS | 31.6034 | 88174 | PCHJ132 132.00 | T1 | PCHJ132 | PCHJ132T1 | 30.6073 | PCHJ132 132.00 | T1 | PCHJ132 | PCHJ132T1 | 30.6073 | 88174 | AMID132T4
[5 empty] | 96152 | T3 | 48.2 | AMID132 | AMID132T3 | NS | 31.9555 | 88174 | PCHJ132 132.00 | T2 | PCHJ132 | PCHJ132T2 | 30.6476 | PCHJ132 132.00 | T2 | PCHJ132 | PCHJ132T2 | 30.6476 | 88174 | AMID132T3
[5 empty] | 96152 | T2 | 48.2 | AMID132 | AMID132T2 | NS | 7.4691 | 88174 | PCHJ132 132.00 | T3 | PCHJ132 | PCHJ132T3 | 5.0594 | PCHJ132 132.00 | T3 | PCHJ132 | PCHJ132T3 | 5.0594 | 88174 | AMID132T2
[5 empty] | 96152 | T1 | 48.2 | AMID132 | AMID132T1 | NS | 6.7225 | 88174 | PCHJ132 132.00 | T4 | PCHJ132 | PCHJ132T4 | 5.0501 | PCHJ132 132.00 | T4 | PCHJ132 | PCHJ132T4 | 5.0501 | 88174 | AMID132T1
[5 empty] | 96156 | T4 | 48.2 | MTIN132 | MTIN132T4 | NS | 19.9934 | 51103 | PCHP132 132.00 | T3 | PCHP132 | PCHP132T3 | 25.6452 | PCHP132 132.00 | T3 | PCHP132 | PCHP132T3 | 25.6452 | 51103 | MTIN132T4
[5 empty] | 96156 | T3 | 48.2 | MTIN132 | MTIN132T3 | NS | 0 | 551103 | PCHP132R 132.00 | T1 | PCHP132 | PCHP132T1 | 46.1988 | PCHP132R 132.00 | T1 | PCHP132 | PCHP132T1 | 46.1988 | 551103 | MTIN132T3
[5 empty] | 96188 | T4 | 48.2 | PJAM132 | PJAM132T4 | NS | 2.9615 | 551103 | PCHP132R 132.00 | T2 | PCHP132 | PCHP132T2 | 46.3707 | PCHP132R 132.00 | T2 | PCHP132 | PCHP132T2 | 46.3707 | 551103 | PJAM132T4
[5 empty] | 96188 | T3 | 48.2 | PJAM132 | PJAM132T3 | NS | 2.7751 | 63102 | PCTY132 132.00 | T1 | PCTY132 | PCTY132T1 | 7.8646 | PCTY132 132.00 | T1 | PCTY132 | PCTY132T1 | 7.8646 | 63102 | PJAM132T3
[5 empty] | 96188 | T2 | 48.2 | PJAM132 | PJAM132T2 | NS | 7.1501 | 63102 | PCTY132 132.00 | T2 | PCTY132 | PCTY132T2 | 12.3877 | PCTY132 132.00 | T2 | PCTY132 | PCTY132T2 | 12.3877 | 63102 | PJAM132T2
[5 empty] | 96188 | T1 | 48.2 | PJAM132 | PJAM132T1 | NS | 7.5716 | 63102 | PCTY132 132.00 | T3 | PCTY132 | PCTY132T3 | 7.3179 | PCTY132 132.00 | T3 | PCTY132 | PCTY132T3 | 7.3179 | 63102 | PJAM132T1
[5 empty] | 51092 | T2 | 48.2 | KEST132 | KEST132T2 | WPKL | 45.7483 | 63102 | PCTY132 132.00 | T4 | PCTY132 | PCTY132T4 | 10.1717 | PCTY132 132.00 | T4 | PCTY132 | PCTY132T4 | 10.1717 | 63102 | KEST132T2
[5 empty] | 51092 | T1 | 48.2 | KEST132 | KEST132T1 | WPKL | 45.9347 | 51049 | PIDH132 132.00 | T1 | PIDH132 | PIDH132T1 | 41.4728 | PIDH132 132.00 | T1 | PIDH132 | PIDH132T1 | 41.4728 | 51049 | KEST132T1
[5 empty] | 51054 | T2 | 48.2 | SMYH132 | SMYH132T2 | SELANGOR | 12.1516 | 51049 | PIDH132 132.00 | T2 | PIDH132 | PIDH132T2 | 41.335 | PIDH132 132.00 | T2 | PIDH132 | PIDH132T2 | 41.335 | 51049 | SMYH132T2
[5 empty] | 51054 | T1 | 48.2 | SMYH132 | SMYH132T1 | SELANGOR | 8.4383 | 51049 | PIDH132 132.00 | T3 | PIDH132 | PIDH132T3 | 6.8778 | PIDH132 132.00 | T3 | PIDH132 | PIDH132T3 | 6.8778 | 51049 | SMYH132T1
[5 empty] | 51053 | T6 | 48.2 | BRNG132 | BRNG132T6 | SELANGOR | 33.6754 | 51049 | PIDH132 132.00 | T4 | PIDH132 | PIDH132T4 | 12.9344 | PIDH132 132.00 | T4 | PIDH132 | PIDH132T4 | 12.9344 | 51049 | BRNG132T4
[5 empty] | 51053 | T5 | 48.2 | BRNG132 | BRNG132T5 | SELANGOR | 34.0006 | 51049 | PIDH132 132.00 | T5 | PIDH132 | PIDH132T5 | 39.992 | PIDH132 132.00 | T5 | PIDH132 | PIDH132T5 | 39.992 | 51049 | BRNG132T3
[5 empty] | 51053 | T2 | 48.2 | BRNG132 | BRNG132T2 | SELANGOR | 19.6879 | 51049 | PIDH132 132.00 | T6 | PIDH132 | PIDH132T6 | 38.1726 | PIDH132 132.00 | T6 | PIDH132 | PIDH132T6 | 38.1726 | 51049 | BRNG132T2
[5 empty] | 51053 | T1 | 48.2 | BRNG132 | BRNG132T1 | SELANGOR | 0 | 51082 | PJST132 132.00 | T1 | PJST132 | PJST132T1 | 26.5398 | PJST132 132.00 | T1 | PJST132 | PJST132T1 | 26.5398 | 51082 | BRNG132T1
[5 empty] | 88114 | T2 | 48.2 | BMKM132 | BMKM132T2 | WPKL | 14.1749 | 51082 | PJST132 132.00 | T2 | PJST132 | PJST132T2 | 26.5481 | PJST132 132.00 | T2 | PJST132 | PJST132T2 | 26.5481 | 51082 | BMKM132T2
[5 empty] | 88114 | T1 | 48.2 | BMKM132 | BMKM132T1 | WPKL | 14.1749 | 51082 | PJST132 132.00 | T3 | PJST132 | PJST132T3 | 8.6257 | PJST132 132.00 | T3 | PJST132 | PJST132T3 | 8.6257 | 51082 | BMKM132T1
[5 empty] | 97116 | T4 | 48.2 | KTGI132 | KTGI132T4 | JOHOR | 5.8112 | 51082 | PJST132 132.00 | T4 | PJST132 | PJST132T4 | 11.2217 | PJST132 132.00 | T4 | PJST132 | PJST132T4 | 11.2217 | 51082 | KTGI132T4
[5 empty] | 97116 | T3 | 48.2 | KTGI132 | KTGI132T3 | JOHOR | 8.3233 | 51015 | PKLG132 132.00 | N1 | PKLG132 | PKLG132N1 | 7.9495 | PKLG132 132.00 | N1 | PKLG132 | PKLG132N1 | 7.9495 | 51015 | KTGI132T3
[5 empty] | 97188 | T4 | 48.2 | UTRM132 | UTRM132T4 | JOHOR | 29.6836 | 51015 | PKLG132 132.00 | N2 | PKLG132 | PKLG132N2 | 7.8822 | PKLG132 132.00 | N2 | PKLG132 | PKLG132N2 | 7.8822 | 51015 | UTRM132T4
[5 empty] | 97188 | T3 | 48.2 | UTRM132 | UTRM132T3 | JOHOR | 30.5555 | 51015 | PKLG132 132.00 | N3 | PKLG132 | PKLG132N3 | 0 | PKLG132 132.00 | N3 | PKLG132 | PKLG132N3 | 0 | 51015 | UTRM132T3
[5 empty] | 97188 | T2 | 48.2 | UTRM132 | UTRM132T2 | JOHOR | 9.3102 | 51015 | PKLG132 132.00 | T1 | PKLG132 | PKLG132T1 | 0 | PKLG132 132.00 | T1 | PKLG132 | PKLG132T1 | 0 | 51015 | UTRM132T2
[5 empty] | 97188 | T1 | 48.2 | UTRM132 | UTRM132T1 | JOHOR | 9.2791 | 51015 | PKLG132 132.00 | T2 | PKLG132 | PKLG132T2 | 0 | PKLG132 132.00 | T2 | PKLG132 | PKLG132T2 | 0 | 51015 | UTRM132T1
[5 empty] | 97118 | T2 | 48.2 | PUBB132 | PUBB132T2 | JOHOR | 10.2514 | 51042 | PMRN132 132.00 | T1 | PMRN132 | PMRN132T1 | 13.0421 | PMRN132 132.00 | T1 | PMRN132 | PMRN132T1 | 13.0421 | 51042 | PUBB132T2
[5 empty] | 97118 | T1 | 48.2 | PUBB132 | PUBB132T1 | JOHOR | 10.1582 | 51042 | PMRN132 132.00 | T2 | PMRN132 | PMRN132T2 | 14.1636 | PMRN132 132.00 | T2 | PMRN132 | PMRN132T2 | 14.1636 | 51042 | PUBB132T1
[5 empty] | 97198 | T2 | 48.2 | PLGI132 | PLGI132T2 | JOHOR | 29.2052 | 51042 | PMRN132 132.00 | T3 | PMRN132 | PMRN132T3 | 47.7158 | PMRN132 132.00 | T3 | PMRN132 | PMRN132T3 | 47.7158 | 51042 | PLGI132T2
[5 empty] | 97198 | T1 | 48.2 | PLGI132 | PLGI132T1 | JOHOR | 29.0561 | 51042 | PMRN132 132.00 | T4 | PMRN132 | PMRN132T4 | 47.8411 | PMRN132 132.00 | T4 | PMRN132 | PMRN132T4 | 47.8411 | 51042 | PLGI132T1
[5 empty] | 97111 | T2 | 48.2 | RNGM132 | RNGM132T2 | JOHOR | 4.4765 | 51039 | PNGA132 132.00 | T1 | PNGA132 | PNGA132T1 | 35.267 | PNGA132 132.00 | T1 | PNGA132 | PNGA132T1 | 35.267 | 51039 | RNGM132T2
[5 empty] | 97111 | T1 | 48.2 | RNGM132 | RNGM132T1 | JOHOR | 4.3905 | 51039 | PNGA132 132.00 | T2 | PNGA132 | PNGA132T2 | 35.3333 | PNGA132 132.00 | T2 | PNGA132 | PNGA132T2 | 35.3333 | 51039 | RNGM132T1
[5 empty] | 97149 | T4 | 48.2 | KLID132 | KLID132T4 | JOHOR | 10.1158 | 51009 | PROT132 132.00 | T1 | PROT132 | PROT132T1 | 32.4039 | PROT132 132.00 | T1 | PROT132 | PROT132T1 | 32.4039 | 51009 | KLID132T4
[5 empty] | 97149 | T3 | 48.2 | KLID132 | KLID132T3 | JOHOR | 6.3331 | 51009 | PROT132 132.00 | T2 | PROT132 | PROT132T2 | 32.2796 | PROT132 132.00 | T2 | PROT132 | PROT132T2 | 32.2796 | 51009 | KLID132T3
[5 empty] | 97149 | T2 | 48.2 | KLID132 | KLID132T2 | JOHOR | 10.852 | 51009 | PROT132 132.00 | T3 | PROT132 | PROT132T3 | 49.7164 | PROT132 132.00 | T3 | PROT132 | PROT132T3 | 49.7164 | 51009 | KLID132T2
[5 empty] | 97149 | T1 | 48.2 | KLID132 | KLID132T1 | JOHOR | 10.1261 | 88176 | PTAI132 132.00 | T1 | PTAI132 | PTAI132T1 | 0 | PTAI132 132.00 | T1 | PTAI132 | PTAI132T1 | 0 | 88176 | KLID132T1
[5 empty] | 97131 | T4 | 48.2 | MSNG132 | MSNG132T4 | JOHOR | 6.8291 | 88176 | PTAI132 132.00 | T2 | PTAI132 | PTAI132T2 | 0 | PTAI132 132.00 | T2 | PTAI132 | PTAI132T2 | 0 | 88176 | MSNG132T4
[5 empty] | 97131 | T3 | 48.2 | MSNG132 | MSNG132T3 | JOHOR | 6.8384 | 88176 | PTAI132 132.00 | T3 | PTAI132 | PTAI132T3 | 34.8342 | PTAI132 132.00 | T3 | PTAI132 | PTAI132T3 | 34.8342 | 88176 | MSNG132T3
[5 empty] | 97131 | T2 | 48.2 | MSNG132 | MSNG132T2 | JOHOR | 3.8686 | 88176 | PTAI132 132.00 | T4 | PTAI132 | PTAI132T4 | 34.5877 | PTAI132 132.00 | T4 | PTAI132 | PTAI132T4 | 34.5877 | 88176 | MSNG132T2
[5 empty] | 97131 | T1 | 48.2 | MSNG132 | MSNG132T1 | JOHOR | 2.8311 | 51052 | RSID132 132.00 | T1 | RSID132 | RSID132T1 | 16.4002 | RSID132 132.00 | T1 | RSID132 | RSID132T1 | 16.4002 | 51052 | MSNG132T1
[5 empty] | 74133 | T2 | 48.2 | TGMK132 | TGMK132T2 | PAHANG | 13.7411 | 51052 | RSID132 132.00 | T2 | RSID132 | RSID132T2 | 16.3112 | RSID132 132.00 | T2 | RSID132 | RSID132T2 | 16.3112 | 51052 | TGMK132T2
[5 empty] | 74133 | T1 | 48.2 | TGMK132 | TGMK132T1 | PAHANG | 13.7514 | 51218 | RWSS132 132.00 | T1 | RWSS132 | RWSS132T1 | 6.2586 | RWSS132 132.00 | T1 | RWSS132 | RWSS132T1 | 6.2586 | 51218 | TGMK132T1
[5 empty] | 97138 | T2 | 48.2 | NYOR132 | NYOR132T2 | JOHOR | 16.6104 | 51034 | SBSR132 132.00 | T1 | SBSR132 | SBSR132T1 | 14.1739 | SBSR132 132.00 | T1 | SBSR132 | SBSR132T1 | 14.1739 | 51034 | NYOR132T2
[5 empty] | 97138 | T1 | 48.2 | NYOR132 | NYOR132T1 | JOHOR | 11.3926 | 51034 | SBSR132 132.00 | T2 | SBSR132 | SBSR132T2 | 12.9406 | SBSR132 132.00 | T2 | SBSR132 | SBSR132T2 | 12.9406 | 51034 | NYOR132T1
[5 empty] | 61137 | T2 | 48.1 | KGAR132 | KGAR132T2 | PERLIS | 11.7281 | 51034 | SBSR132 132.00 | T3 | SBSR132 | SBSR132T3 | 24.0464 | SBSR132 132.00 | T3 | SBSR132 | SBSR132T3 | 24.0464 | 51034 | KGAR132T2
[5 empty] | 61137 | T1 | 48.1 | KGAR132 | KGAR132T1 | PERLIS | 12.0377 | 51034 | SBSR132 132.00 | T4 | SBSR132 | SBSR132T4 | 23.5576 | SBSR132 132.00 | T4 | SBSR132 | SBSR132T4 | 23.5576 | 51034 | KGAR132T1
[5 empty] | 63111 | T4 | 48.1 | SIKD132 | SIKD132T4 | PERAK | 23.9211 | 51032 | SDCA132 132.00 | T1 | SDCA132 | SDCA132T1 | 17.6004 | SDCA132 132.00 | T1 | SDCA132 | SDCA132T1 | 17.6004 | 51032 | SIKD132T4
[5 empty] | 63111 | T3 | 48.1 | SIKD132 | SIKD132T3 | PERAK | 23.8703 | 51032 | SDCA132 132.00 | T2 | SDCA132 | SDCA132T2 | 17.6449 | SDCA132 132.00 | T2 | SDCA132 | SDCA132T2 | 17.6449 | 51032 | SIKD132T3
[5 empty] | 51085 | T4 | 48.1 | LKDG132 | LKDG132T4 | SELANGOR | 28.47 | 51027 | SHAB132 132.00 | T1 | SHAB132 | SHAB132T1 | 25.2341 | SHAB132 132.00 | T1 | SHAB132 | SHAB132T1 | 25.2341 | 51027 | LKDG132T4
[5 empty] | 51085 | T3 | 48.1 | LKDG132 | LKDG132T3 | SELANGOR | 28.645 | 51027 | SHAB132 132.00 | T2 | SHAB132 | SHAB132T2 | 26.0252 | SHAB132 132.00 | T2 | SHAB132 | SHAB132T2 | 26.0252 | 51027 | LKDG132T3
[5 empty] | 51075 | T2 | 48.1 | SJTC132 | SJTC132T2 | SELANGOR | 28.5301 | 51017 | SHAE132 132.00 | T1 | SHAE132 | SHAE132T1 | 2.3765 | SHAE132 132.00 | T1 | SHAE132 | SHAE132T1 | 2.3765 | 51017 | SJTC132T2
[5 empty] | 51075 | T1 | 48.1 | SJTC132 | SJTC132T1 | SELANGOR | 28.4607 | 51017 | SHAE132 132.00 | T2 | SHAE132 | SHAE132T2 | 5.6756 | SHAE132 132.00 | T2 | SHAE132 | SHAE132T2 | 5.6756 | 51017 | SJTC132T1
[5 empty] | 62131 | T2 | 48.1 | BBRU132 | BBRU132T2 | P PINANG | 48.1662 | 51017 | SHAE132 132.00 | T3 | SHAE132 | SHAE132T3 | 23.7854 | SHAE132 132.00 | T3 | SHAE132 | SHAE132T3 | 23.7854 | 51017 | BBRU132T2
[5 empty] | 62131 | T1 | 48.1 | BBRU132 | BBRU132T1 | P PINANG | 48.453 | 51017 | SHAE132 132.00 | T4 | SHAE132 | SHAE132T4 | 24.0681 | SHAE132 132.00 | T4 | SHAE132 | SHAE132T4 | 24.0681 | 51017 | BBRU132T1
[5 empty] | 96133 | T2 | 48.1 | SMRK132 | SMRK132T2 | NS | 10.8013 | 51017 | SHAE132 132.00 | T5 | SHAE132 | SHAE132T5 | 32.8543 | SHAE132 132.00 | T5 | SHAE132 | SHAE132T5 | 32.8543 | 51017 | SMRK132T2
[5 empty] | 96133 | T1 | 48.1 | SMRK132 | SMRK132T1 | NS | 11.5406 | 51003 | SHAN132 132.00 | T1 | SHAN132 | SHAN132T1 | 0 | SHAN132 132.00 | T1 | SHAN132 | SHAN132T1 | 0 | 51003 | SMRK132T1
[5 empty] | 96194 | F4 | 48.1 | HLNN132 | HLNN132F4 | NS | 0 | 51003 | SHAN132 132.00 | T2 | SHAN132 | SHAN132T2 | 0.007 | SHAN132 132.00 | T2 | SHAN132 | SHAN132T2 | 0.007 | 51003 | HLNN132F4
[5 empty] | 96194 | F3 | 48.1 | HLNN132 | HLNN132F3 | NS | 10.8686 | 51003 | SHAN132 132.00 | T3 | SHAN132 | SHAN132T3 | 0 | SHAN132 132.00 | T3 | SHAN132 | SHAN132T3 | 0 | 51003 | HLNN132F3
[5 empty] | 96194 | F2 | 48.1 | HLNN132 | HLNN132F2 | NS | 10.7143 | 51007 | SHAS132 132.00 | T1 | SHAS132 | SHAS132T1 | 38.9275 | SHAS132 132.00 | T1 | SHAS132 | SHAS132T1 | 38.9275 | 51007 | HLNN132F2
[5 empty] | 96194 | F1 | 48.1 | HLNN132 | HLNN132F1 | NS | 0.1118 | 51007 | SHAS132 132.00 | T2 | SHAS132 | SHAS132T2 | 39.0476 | SHAS132 132.00 | T2 | SHAS132 | SHAS132T2 | 39.0476 | 51007 | HLNN132F1
[5 empty] | 97142 | T2 | 48.1 | SELG132 | SELG132T2 | JOHOR | 14.6927 | 51041 | SHAW132 132.00 | T1 | SHAW132 | SHAW132T1 | 9.2294 | SHAW132 132.00 | T1 | SHAW132 | SHAW132T1 | 9.2294 | 51041 | SELG132T2
[5 empty] | 97142 | T1 | 48.1 | SELG132 | SELG132T1 | JOHOR | 14.6927 | 51041 | SHAW132 132.00 | T2 | SHAW132 | SHAW132T2 | 5.8288 | SHAW132 132.00 | T2 | SHAW132 | SHAW132T2 | 5.8288 | 51041 | SELG132T1
[5 empty] | 97152 | T2 | 48.1 | STUL132 | STUL132T2 | JOHOR | 5.2779 | 51041 | SHAW132 132.00 | T3 | SHAW132 | SHAW132T3 | 28.5911 | SHAW132 132.00 | T3 | SHAW132 | SHAW132T3 | 28.5911 | 51041 | STUL132T2
[5 empty] | 97152 | T1 | 48.1 | STUL132 | STUL132T1 | JOHOR | 5.2914 | 51041 | SHAW132 132.00 | T4 | SHAW132 | SHAW132T4 | 28.4565 | SHAW132 132.00 | T4 | SHAW132 | SHAW132T4 | 28.4565 | 51041 | STUL132T1
[5 empty] | 97146 | T4 | 48.1 | SGAD132 | SGAD132T4 | JOHOR | 10.7537 | 51002 | SHLB132 132.00 | T1 | SHLB132 | SHLB132T1 | 27.4096 | SHLB132 132.00 | T1 | SHLB132 | SHLB132T1 | 27.4096 | 51002 | SGAD132T4
[5 empty] | 97146 | T3 | 48.1 | SGAD132 | SGAD132T3 | JOHOR | 11.9062 | 51002 | SHLB132 132.00 | T2 | SHLB132 | SHLB132T2 | 27.5132 | SHLB132 132.00 | T2 | SHLB132 | SHLB132T2 | 27.5132 | 51002 | SGAD132T3
[5 empty] | 97146 | T2 | 48.1 | SGAD132 | SGAD132T2 | JOHOR | 8.7023 | 51075 | SJTC132 132.00 | T1 | SJTC132 | SJTC132T1 | 28.4607 | SJTC132 132.00 | T1 | SJTC132 | SJTC132T1 | 28.4607 | 51075 | SGAD132T2
[5 empty] | 97146 | T1 | 48.1 | SGAD132 | SGAD132T1 | JOHOR | 15.2177 | 51075 | SJTC132 132.00 | T2 | SJTC132 | SJTC132T2 | 28.5301 | SJTC132 132.00 | T2 | SJTC132 | SJTC132T2 | 28.5301 | 51075 | SGAD132T1
[5 empty] | 97103 | T4 | 48.1 | PJML132 | PJML132T4 | JOHOR | 9.5804 | 51054 | SMYH132 132.00 | T1 | SMYH132 | SMYH132T1 | 8.4383 | SMYH132 132.00 | T1 | SMYH132 | SMYH132T1 | 8.4383 | 51054 | PJML132T4
[5 empty] | 97103 | T3 | 48.1 | PJML132 | PJML132T3 | JOHOR | 9.6156 | 51054 | SMYH132 132.00 | T2 | SMYH132 | SMYH132T2 | 12.1516 | SMYH132 132.00 | T2 | SMYH132 | SMYH132T2 | 12.1516 | 51054 | PJML132T3
[5 empty] | 97104 | T2 | 48.1 | PYSF132 | PYSF132T2 | JOHOR | 3.9867 | 51030 | SRDG132 132.00 | T1 | SRDG132 | SRDG132T1 | 30.2914 | SRDG132 132.00 | T1 | SRDG132 | SRDG132T1 | 30.2914 | 51030 | PYSF132T2
[5 empty] | 97104 | T1 | 48.1 | PYSF132 | PYSF132T1 | JOHOR | 4.0208 | 51030 | SRDG132 132.00 | T2 | SRDG132 | SRDG132T2 | 0 | SRDG132 132.00 | T2 | SRDG132 | SRDG132T2 | 0 | 51030 | PYSF132T1
[5 empty] | 97120 | T2 | 48.1 | PSRI132 | PSRI132T2 | JOHOR | 16.16 | 51029 | SSWW132 132.00 | T1 | SSWW132 | SSWW132T1 | 0 | SSWW132 132.00 | T1 | SSWW132 | SSWW132T1 | 0 | 51029 | PSRI132T2
[5 empty] | 97120 | T1 | 48.1 | PSRI132 | PSRI132T1 | JOHOR | 6.8032 | 51029 | SSWW132 132.00 | T2 | SSWW132 | SSWW132T2 | 9.4634 | SSWW132 132.00 | T2 | SSWW132 | SSWW132T2 | 9.4634 | 51029 | PSRI132T1
[5 empty] | 97125 | T4 | 48.1 | SSLG132 | SSLG132T4 | JOHOR | 4.5106 | 51013 | STIA132 132.00 | T1 | STIA132 | STIA132T1 | 33.1173 | STIA132 132.00 | T1 | STIA132 | STIA132T1 | 33.1173 | 51013 | SSLG132T4
[5 empty] | 97125 | T3 | 48.1 | SSLG132 | SSLG132T3 | JOHOR | 4.5013 | 51013 | STIA132 132.00 | T2 | STIA132 | STIA132T2 | 36.9797 | STIA132 132.00 | T2 | STIA132 | STIA132T2 | 36.9797 | 51013 | SSLG132T3
[12 empty] | 51020 | TJYA132 132.00 | T1 | TJYA132 | TJYA132T1 | 26.4901 | TJYA132 132.00 | T1 | TJYA132 | TJYA132T1 | 26.4901 | 51020
[12 empty] | 51020 | TJYA132 132.00 | T2 | TJYA132 | TJYA132T2 | 26.8805 | TJYA132 132.00 | T2 | TJYA132 | TJYA132T2 | 26.8805 | 51020
[12 empty] | 51020 | TJYA132 132.00 | T3 | TJYA132 | TJYA132T3 | 16.2263 | TJYA132 132.00 | T3 | TJYA132 | TJYA132T3 | 16.2263 | 51020
[12 empty] | 51084 | TMSY132 132.00 | T1 | TMSY132 | TMSY132T1 | 15.5138 | TMSY132 132.00 | T1 | TMSY132 | TMSY132T1 | 15.5138 | 51084
[12 empty] | 51084 | TMSY132 132.00 | T2 | TMSY132 | TMSY132T2 | 15.4766 | TMSY132 132.00 | T2 | TMSY132 | TMSY132T2 | 15.4766 | 51084
[12 empty] | 51084 | TMSY132 132.00 | T3 | TMSY132 | TMSY132T3 | 1.6351 | TMSY132 132.00 | T3 | TMSY132 | TMSY132T3 | 1.6351 | 51084
[12 empty] | 51084 | TMSY132 132.00 | T4 | TMSY132 | TMSY132T4 | 2.3009 | TMSY132 132.00 | T4 | TMSY132 | TMSY132T4 | 2.3009 | 51084
[12 empty] | 51051 | TPGR132 132.00 | T1 | TPGR132 | TPGR132T1 | 16.6135 | TPGR132 132.00 | T1 | TPGR132 | TPGR132T1 | 16.6135 | 51051
[12 empty] | 51051 | TPGR132 132.00 | T2 | TPGR132 | TPGR132T2 | 9.2201 | TPGR132 132.00 | T2 | TPGR132 | TPGR132T2 | 9.2201 | 51051
[12 empty] | 51051 | TPGR132 132.00 | T3 | TPGR132 | TPGR132T3 | 45.2886 | TPGR132 132.00 | T3 | TPGR132 | TPGR132T3 | 45.2886 | 51051
[12 empty] | 51051 | TPGR132 132.00 | T4 | TPGR132 | TPGR132T4 | 45.5454 | TPGR132 132.00 | T4 | TPGR132 | TPGR132T4 | 45.5454 | 51051
[12 empty] | 51100 | UYAM132 132.00 | T1 | UYAM132 | UYAM132T1 | 11.7146 | UYAM132 132.00 | T1 | UYAM132 | UYAM132T1 | 11.7146 | 51100
[12 empty] | 51100 | UYAM132 132.00 | T2 | UYAM132 | UYAM132T2 | 12.6569 | UYAM132 132.00 | T2 | UYAM132 | UYAM132T2 | 12.6569 | 51100
[12 empty] | 51100 | UYAM132 132.00 | T3 | UYAM132 | UYAM132T3 | 3.7961 | UYAM132 132.00 | T3 | UYAM132 | UYAM132T3 | 3.7961 | 51100
[12 empty] | 51100 | UYAM132 132.00 | T4 | UYAM132 | UYAM132T4 | 3.763 | UYAM132 132.00 | T4 | UYAM132 | UYAM132T4 | 3.763 | 51100
[12 empty] | 51046 | VMBR132 132.00 | T1 | VMBR132 | VMBR132T1 | 41.5328 | VMBR132 132.00 | T1 | VMBR132 | VMBR132T1 | 41.5328 | 51046
[12 empty] | 51046 | VMBR132 132.00 | T2 | VMBR132 | VMBR132T2 | 41.0751 | VMBR132 132.00 | T2 | VMBR132 | VMBR132T2 | 41.0751 | 51046
[12 empty] | 51061 | ABBA132 132.00 | T5 | ABBA132 | ABBA132T5 | 17.3229 | ABBA132 132.00 | T5 | ABBA132 | ABBA132T5 | 17.3229 | 51061
[12 empty] | 51061 | ABBA132 132.00 | T6 | ABBA132 | ABBA132T6 | 17.3322 | ABBA132 132.00 | T6 | ABBA132 | ABBA132T6 | 17.3322 | 51061
[12 empty] | 51142 | AMDC132 132.00 | T1 | AMDC132 | AMDC132T1 | 0.3925 | AMDC132 132.00 | T1 | AMDC132 | AMDC132T1 | 0.3925 | 51142
[12 empty] | 51142 | AMDC132 132.00 | T2 | AMDC132 | AMDC132T2 | 0.9299 | AMDC132 132.00 | T2 | AMDC132 | AMDC132T2 | 0.9299 | 51142
[12 empty] | 88120 | AMPG132 132.00 | T3 | AMPG132 | AMPG132T3 | 42.5704 | AMPG132 132.00 | T3 | AMPG132 | AMPG132T3 | 42.5704 | 88120
[12 empty] | 88120 | AMPG132 132.00 | T4 | AMPG132 | AMPG132T4 | 42.4761 | AMPG132 132.00 | T4 | AMPG132 | AMPG132T4 | 42.4761 | 88120
[12 empty] | 88120 | AMPG132 132.00 | T5 | AMPG132 | AMPG132T5 | 30.0233 | AMPG132 132.00 | T5 | AMPG132 | AMPG132T5 | 30.0233 | 88120
[12 empty] | 88120 | AMPG132 132.00 | T6 | AMPG132 | AMPG132T6 | 29.4548 | AMPG132 132.00 | T6 | AMPG132 | AMPG132T6 | 29.4548 | 88120
[12 empty] | 88123 | BBCC132 132.00 | T1 | BBCC132 | BBCC132T1 | 4.1254 | BBCC132 132.00 | T1 | BBCC132 | BBCC132T1 | 4.1254 | 88123
[12 empty] | 88123 | BBCC132 132.00 | T2 | BBCC132 | BBCC132T2 | 4.1648 | BBCC132 132.00 | T2 | BBCC132 | BBCC132T2 | 4.1648 | 88123
[12 empty] | 88141 | BFLD132 132.00 | T1 | BFLD132 | BFLD132T1 | 22.2001 | BFLD132 132.00 | T1 | BFLD132 | BFLD132T1 | 22.2001 | 88141
[12 empty] | 88141 | BFLD132 132.00 | T2 | BFLD132 | BFLD132T2 | 22.55 | BFLD132 132.00 | T2 | BFLD132 | BFLD132T2 | 22.55 | 88141
[12 empty] | 88114 | BMKM132 132.00 | T1 | BMKM132 | BMKM132T1 | 14.1749 | BMKM132 132.00 | T1 | BMKM132 | BMKM132T1 | 14.1749 | 88114
[12 empty] | 88114 | BMKM132 132.00 | T2 | BMKM132 | BMKM132T2 | 14.1749 | BMKM132 132.00 | T2 | BMKM132 | BMKM132T2 | 14.1749 | 88114
[12 empty] | 51053 | BRNG132 132.00 | T5 | BRNG132 | BRNG132T5 | 34.0006 | BRNG132 132.00 | T5 | BRNG132 | BRNG132T5 | 34.0006 | 51053
[12 empty] | 51053 | BRNG132 132.00 | T6 | BRNG132 | BRNG132T6 | 33.6754 | BRNG132 132.00 | T6 | BRNG132 | BRNG132T6 | 33.6754 | 51053
[12 empty] | 88136 | BTRZ132 132.00 | T1 | BTRZ132 | BTRZ132T1 | 15.6692 | BTRZ132 132.00 | T1 | BTRZ132 | BTRZ132T1 | 15.6692 | 88136
[12 empty] | 88136 | BTRZ132 132.00 | T2 | BTRZ132 | BTRZ132T2 | 0 | BTRZ132 132.00 | T2 | BTRZ132 | BTRZ132T2 | 0 | 88136
[12 empty] | 88136 | BTRZ132 132.00 | T3 | BTRZ132 | BTRZ132T3 | 41.1642 | BTRZ132 132.00 | T3 | BTRZ132 | BTRZ132T3 | 41.1642 | 88136
[12 empty] | 88136 | BTRZ132 132.00 | T4 | BTRZ132 | BTRZ132T4 | 41.4603 | BTRZ132 132.00 | T4 | BTRZ132 | BTRZ132T4 | 41.4603 | 88136
[12 empty] | 51089 | CBJC132 132.00 | T2 | CBJC132 | CBJC132T2 | 27.3071 | CBJC132 132.00 | T2 | CBJC132 | CBJC132T2 | 27.3071 | 51089
[12 empty] | 51089 | CBJC132 132.00 | T3 | CBJC132 | CBJC132T3 | 6.2461 | CBJC132 132.00 | T3 | CBJC132 | CBJC132T3 | 6.2461 | 51089
[12 empty] | 51089 | CBJC132 132.00 | T4 | CBJC132 | CBJC132T4 | 6.2161 | CBJC132 132.00 | T4 | CBJC132 | CBJC132T4 | 6.2161 | 51089
[12 empty] | 88164 | COCH132 132.00 | T1 | COCH132 | COCH132T1 | 4.784 | COCH132 132.00 | T1 | COCH132 | COCH132T1 | 4.784 | 88164
[12 empty] | 88164 | COCH132 132.00 | T2 | COCH132 | COCH132T2 | 4.7736 | COCH132 132.00 | T2 | COCH132 | COCH132T2 | 4.7736 | 88164
[12 empty] | 88104 | DCTY132 132.00 | T1 | DCTY132 | DCTY132T1 | 12.8951 | DCTY132 132.00 | T1 | DCTY132 | DCTY132T1 | 12.8951 | 88104
[12 empty] | 88104 | DCTY132 132.00 | T2 | DCTY132 | DCTY132T2 | 12.9489 | DCTY132 132.00 | T2 | DCTY132 | DCTY132T2 | 12.9489 | 88104
[12 empty] | 88195 | DDSA132 132.00 | T1 | DDSA132 | DDSA132T1 | 7.1957 | DDSA132 132.00 | T1 | DDSA132 | DDSA132T1 | 7.1957 | 88195
[12 empty] | 88195 | DDSA132 132.00 | T2 | DDSA132 | DDSA132T2 | 5.804 | DDSA132 132.00 | T2 | DDSA132 | DDSA132T2 | 5.804 | 88195
[12 empty] | 88195 | DDSA132 132.00 | T3 | DDSA132 | DDSA132T3 | 30.6777 | DDSA132 132.00 | T3 | DDSA132 | DDSA132T3 | 30.6777 | 88195
[12 empty] | 88195 | DDSA132 132.00 | T4 | DDSA132 | DDSA132T4 | 30.6943 | DDSA132 132.00 | T4 | DDSA132 | DDSA132T4 | 30.6943 | 88195
[12 empty] | 88112 | DMHT132 132.00 | T1 | DMHT132 | DMHT132T1 | 15.1669 | DMHT132 132.00 | T1 | DMHT132 | DMHT132T1 | 15.1669 | 88112
[12 empty] | 88112 | DMHT132 132.00 | T2 | DMHT132 | DMHT132T2 | 15.0996 | DMHT132 132.00 | T2 | DMHT132 | DMHT132T2 | 15.0996 | 88112
[12 empty] | 88112 | DMHT132 132.00 | T3 | DMHT132 | DMHT132T3 | 6.6458 | DMHT132 132.00 | T3 | DMHT132 | DMHT132T3 | 6.6458 | 88112
[12 empty] | 88112 | DMHT132 132.00 | T4 | DMHT132 | DMHT132T4 | 6.621 | DMHT132 132.00 | T4 | DMHT132 | DMHT132T4 | 6.621 | 88112
[12 empty] | 88113 | DWGI132 132.00 | T1 | DWGI132 | DWGI132T1 | 5.9924 | DWGI132 132.00 | T1 | DWGI132 | DWGI132T1 | 5.9924 | 88113
[12 empty] | 88113 | DWGI132 132.00 | T2 | DWGI132 | DWGI132T2 | 5.9407 | DWGI132 132.00 | T2 | DWGI132 | DWGI132T2 | 5.9407 | 88113
[12 empty] | 88133 | GWAY132 132.00 | T1 | GWAY132 | GWAY132T1 | 13.3186 | GWAY132 132.00 | T1 | GWAY132 | GWAY132T1 | 13.3186 | 88133
[12 empty] | 88133 | GWAY132 132.00 | T2 | GWAY132 | GWAY132T2 | 13.302 | GWAY132 132.00 | T2 | GWAY132 | GWAY132T2 | 13.302 | 88133
[12 empty] | 88156 | HKCK132 132.00 | T1 | HKCK132 | HKCK132T1 | 7.5384 | HKCK132 132.00 | T1 | HKCK132 | HKCK132T1 | 7.5384 | 88156
[12 empty] | 88156 | HKCK132 132.00 | T2 | HKCK132 | HKCK132T2 | 7.877 | HKCK132 132.00 | T2 | HKCK132 | HKCK132T2 | 7.877 | 88156
[12 empty] | 88156 | HKCK132 132.00 | T3 | HKCK132 | HKCK132T3 | 42.1116 | HKCK132 132.00 | T3 | HKCK132 | HKCK132T3 | 42.1116 | 88156
[12 empty] | 88156 | HKCK132 132.00 | T4 | HKCK132 | HKCK132T4 | 41.7016 | HKCK132 132.00 | T4 | HKCK132 | HKCK132T4 | 41.7016 | 88156
[12 empty] | 51219 | ICNC132 132.00 | T1 | ICNC132 | ICNC132T1 | 0 | ICNC132 132.00 | T1 | ICNC132 | ICNC132T1 | 0 | 51219
[12 empty] | 51219 | ICNC132 132.00 | T2 | ICNC132 | ICNC132T2 | 0 | ICNC132 132.00 | T2 | ICNC132 | ICNC132T2 | 0 | 51219
[12 empty] | 88161 | IMBI132 132.00 | T1 | IMBI132 | IMBI132T1 | 3.2194 | IMBI132 132.00 | T1 | IMBI132 | IMBI132T1 | 3.2194 | 88161
[12 empty] | 88161 | IMBI132 132.00 | T2 | IMBI132 | IMBI132T2 | 10.9939 | IMBI132 132.00 | T2 | IMBI132 | IMBI132T2 | 10.9939 | 88161
[12 empty] | 88161 | IMBI132 132.00 | T3 | IMBI132 | IMBI132T3 | 25.4443 | IMBI132 132.00 | T3 | IMBI132 | IMBI132T3 | 25.4443 | 88161
[12 empty] | 88161 | IMBI132 132.00 | T4 | IMBI132 | IMBI132T4 | 25.6182 | IMBI132 132.00 | T4 | IMBI132 | IMBI132T4 | 25.6182 | 88161
[12 empty] | 88161 | IMBI132 132.00 | T5 | IMBI132 | IMBI132T5 | 33.9478 | IMBI132 132.00 | T5 | IMBI132 | IMBI132T5 | 33.9478 | 88161
[12 empty] | 51101 | IOIM132 132.00 | T1 | IOIM132 | IOIM132T1 | 16.6208 | IOIM132 132.00 | T1 | IOIM132 | IOIM132T1 | 16.6208 | 51101
[12 empty] | 51101 | IOIM132 132.00 | T2 | IOIM132 | IOIM132T2 | 16.5214 | IOIM132 132.00 | T2 | IOIM132 | IOIM132T2 | 16.5214 | 51101
[12 empty] | 51066 | JDHL132 132.00 | T1 | JDHL132 | JDHL132T1 | 0 | JDHL132 132.00 | T1 | JDHL132 | JDHL132T1 | 0 | 51066
[12 empty] | 51066 | JDHL132 132.00 | T2 | JDHL132 | JDHL132T2 | 0 | JDHL132 132.00 | T2 | JDHL132 | JDHL132T2 | 0 | 51066
[12 empty] | 88157 | JING132 132.00 | T1 | JING132 | JING132T1 | 0 | JING132 132.00 | T1 | JING132 | JING132T1 | 0 | 88157
[12 empty] | 88157 | JING132 132.00 | T2 | JING132 | JING132T2 | 0 | JING132 132.00 | T2 | JING132 | JING132T2 | 0 | 88157
[12 empty] | 51092 | KEST132 132.00 | T1 | KEST132 | KEST132T1 | 45.9347 | KEST132 132.00 | T1 | KEST132 | KEST132T1 | 45.9347 | 51092
[12 empty] | 51092 | KEST132 132.00 | T2 | KEST132 | KEST132T2 | 45.7483 | KEST132 132.00 | T2 | KEST132 | KEST132T2 | 45.7483 | 51092
[12 empty] | 88146 | KLCC132 132.00 | T3 | KLCC132 | KLCC132T3 | 20.4801 | KLCC132 132.00 | T3 | KLCC132 | KLCC132T3 | 20.4801 | 88146
[12 empty] | 88146 | KLCC132 132.00 | T4 | KLCC132 | KLCC132T4 | 20.4345 | KLCC132 132.00 | T4 | KLCC132 | KLCC132T4 | 20.4345 | 88146
[12 empty] | 588146 | KLCC132R 132.00 | T1 | KLCC132 | KLCC132T1 | 6.3859 | KLCC132R 132.00 | T1 | KLCC132 | KLCC132T1 | 6.3859 | 588146
[12 empty] | 588146 | KLCC132R 132.00 | T2 | KLCC132 | KLCC132T2 | 6.9161 | KLCC132R 132.00 | T2 | KLCC132 | KLCC132T2 | 6.9161 | 588146
[12 empty] | 88121 | KLJT132 132.00 | T1 | KLJT132 | KLJT132T1 | 18.8875 | KLJT132 132.00 | T1 | KLJT132 | KLJT132T1 | 18.8875 | 88121
[12 empty] | 88121 | KLJT132 132.00 | T2 | KLJT132 | KLJT132T2 | 18.8129 | KLJT132 132.00 | T2 | KLJT132 | KLJT132T2 | 18.8129 | 88121
[12 empty] | 88121 | KLJT132 132.00 | T4 | KLJT132 | KLJT132T4 | 18.495 | KLJT132 132.00 | T4 | KLJT132 | KLJT132T4 | 18.495 | 88121
[12 empty] | 88163 | KLPV132 132.00 | T1 | KLPV132 | KLPV132T1 | 28.5694 | KLPV132 132.00 | T1 | KLPV132 | KLPV132T1 | 28.5694 | 88163
[12 empty] | 88163 | KLPV132 132.00 | T2 | KLPV132 | KLPV132T2 | 28.6108 | KLPV132 132.00 | T2 | KLPV132 | KLPV132T2 | 28.6108 | 88163
[12 empty] | 588124 | KULE132R 132.00 | T1 | KULE132 | KULE132T1 | 39.3697 | KULE132R 132.00 | T1 | KULE132 | KULE132T1 | 39.3697 | 588124
[12 empty] | 588124 | KULE132R 132.00 | T2 | KULE132 | KULE132T2 | 39.3707 | KULE132R 132.00 | T2 | KULE132 | KULE132T2 | 39.3707 | 588124
[12 empty] | 88111 | KULN132L 132.00 | T1 | KULN132 | KULN132T1 | 38.272 | KULN132L 132.00 | T1 | KULN132 | KULN132T1 | 38.272 | 88111
[12 empty] | 88111 | KULN132L 132.00 | T2 | KULN132 | KULN132T2 | 38.2026 | KULN132L 132.00 | T2 | KULN132 | KULN132T2 | 38.2026 | 88111
[12 empty] | 588111 | KULN132R 132.00 | T3 | KULN132 | KULN132T3 | 16.6011 | KULN132R 132.00 | T3 | KULN132 | KULN132T3 | 16.6011 | 588111
[12 empty] | 588111 | KULN132R 132.00 | T4 | KULN132 | KULN132T4 | 16.482 | KULN132R 132.00 | T4 | KULN132 | KULN132T4 | 16.482 | 588111
[12 empty] | 88117 | KULS132 132.00 | T1 | KULS132 | KULS132T1 | 12.5948 | KULS132 132.00 | T1 | KULS132 | KULS132T1 | 12.5948 | 88117
[12 empty] | 88117 | KULS132 132.00 | T2 | KULS132 | KULS132T2 | 6.5506 | KULS132 132.00 | T2 | KULS132 | KULS132T2 | 6.5506 | 88117
[12 empty] | 88117 | KULS132 132.00 | T3 | KULS132 | KULS132T3 | 41.9574 | KULS132 132.00 | T3 | KULS132 | KULS132T3 | 41.9574 | 88117
[12 empty] | 88117 | KULS132 132.00 | T4 | KULS132 | KULS132T4 | 41.9077 | KULS132 132.00 | T4 | KULS132 | KULS132T4 | 41.9077 | 88117
[12 empty] | 51081 | MCRS132 132.00 | T1 | MCRS132 | MCRS132T1 | 29.6691 | MCRS132 132.00 | T1 | MCRS132 | MCRS132T1 | 29.6691 | 51081
[12 empty] | 51081 | MCRS132 132.00 | T2 | MCRS132 | MCRS132T2 | 25.7125 | MCRS132 132.00 | T2 | MCRS132 | MCRS132T2 | 25.7125 | 51081
[12 empty] | 88129 | MDAM132 132.00 | T1 | MDAM132 | MDAM132T1 | 18.2683 | MDAM132 132.00 | T1 | MDAM132 | MDAM132T1 | 18.2683 | 88129
[12 empty] | 88129 | MDAM132 132.00 | T2 | MDAM132 | MDAM132T2 | 17.3322 | MDAM132 132.00 | T2 | MDAM132 | MDAM132T2 | 17.3322 | 88129
[12 empty] | 88128 | MJLR132 132.00 | T1 | MJLR132 | MJLR132T1 | 49.94 | MJLR132 132.00 | T1 | MJLR132 | MJLR132T1 | 49.94 | 88128
[12 empty] | 88128 | MJLR132 132.00 | T2 | MJLR132 | MJLR132T2 | 49.3467 | MJLR132 132.00 | T2 | MJLR132 | MJLR132T2 | 49.3467 | 88128
[12 empty] | 88105 | MTRE132 132.00 | T1 | MTRE132 | MTRE132T1 | 9.7119 | MTRE132 132.00 | T1 | MTRE132 | MTRE132T1 | 9.7119 | 88105
[12 empty] | 88105 | MTRE132 132.00 | T2 | MTRE132 | MTRE132T2 | 9.6519 | MTRE132 132.00 | T2 | MTRE132 | MTRE132T2 | 9.6519 | 88105
[12 empty] | 88139 | MVLY132 132.00 | T1 | MVLY132 | MVLY132T1 | 0 | MVLY132 132.00 | T1 | MVLY132 | MVLY132T1 | 0 | 88139
[12 empty] | 88139 | MVLY132 132.00 | T2 | MVLY132 | MVLY132T2 | 0 | MVLY132 132.00 | T2 | MVLY132 | MVLY132T2 | 0 | 88139
[12 empty] | 88139 | MVLY132 132.00 | T3 | MVLY132 | MVLY132T3 | 28.7982 | MVLY132 132.00 | T3 | MVLY132 | MVLY132T3 | 28.7982 | 88139
[12 empty] | 88139 | MVLY132 132.00 | T4 | MVLY132 | MVLY132T4 | 28.6295 | MVLY132 132.00 | T4 | MVLY132 | MVLY132T4 | 28.6295 | 88139
[12 empty] | 88116 | MWSN132 132.00 | T1 | MWSN132 | MWSN132T1 | 1.4311 | MWSN132 132.00 | T1 | MWSN132 | MWSN132T1 | 1.4311 | 88116
[12 empty] | 88116 | MWSN132 132.00 | T2 | MWSN132 | MWSN132T2 | 1.4217 | MWSN132 132.00 | T2 | MWSN132 | MWSN132T2 | 1.4217 | 88116
[12 empty] | 51073 | PJYC132 132.00 | T1 | PJYC132 | PJYC132T1 | 23.6653 | PJYC132 132.00 | T1 | PJYC132 | PJYC132T1 | 23.6653 | 51073
[12 empty] | 51073 | PJYC132 132.00 | T2 | PJYC132 | PJYC132T2 | 23.8517 | PJYC132 132.00 | T2 | PJYC132 | PJYC132T2 | 23.8517 | 51073
[12 empty] | 88175 | PMJU132 132.00 | T1 | PMJU132 | PMJU132T1 | 16.3951 | PMJU132 132.00 | T1 | PMJU132 | PMJU132T1 | 16.3951 | 88175
[12 empty] | 88175 | PMJU132 132.00 | T2 | PMJU132 | PMJU132T2 | 4.4868 | PMJU132 132.00 | T2 | PMJU132 | PMJU132T2 | 4.4868 | 88175
[12 empty] | 88175 | PMJU132 132.00 | T3 | PMJU132 | PMJU132T3 | 37.1154 | PMJU132 132.00 | T3 | PMJU132 | PMJU132T3 | 37.1154 | 88175
[12 empty] | 88175 | PMJU132 132.00 | T4 | PMJU132 | PMJU132T4 | 37.3774 | PMJU132 132.00 | T4 | PMJU132 | PMJU132T4 | 37.3774 | 88175
[12 empty] | 88175 | PMJU132 132.00 | T5 | PMJU132 | PMJU132T5 | 36.0074 | PMJU132 132.00 | T5 | PMJU132 | PMJU132T5 | 36.0074 | 88175
[12 empty] | 88175 | PMJU132 132.00 | T6 | PMJU132 | PMJU132T6 | 35.6936 | PMJU132 132.00 | T6 | PMJU132 | PMJU132T6 | 35.6936 | 88175
[12 empty] | 88119 | PULU132 132.00 | T1 | PULU132 | PULU132T1 | 46.3686 | PULU132 132.00 | T1 | PULU132 | PULU132T1 | 46.3686 | 88119
[12 empty] | 88119 | PULU132 132.00 | T2 | PULU132 | PULU132T2 | 46.1988 | PULU132 132.00 | T2 | PULU132 | PULU132T2 | 46.1988 | 88119
[12 empty] | 88179 | PVBJ132 132.00 | T1 | PVBJ132 | PVBJ132T1 | 17.1147 | PVBJ132 132.00 | T1 | PVBJ132 | PVBJ132T1 | 17.1147 | 88179
[12 empty] | 88179 | PVBJ132 132.00 | T2 | PVBJ132 | PVBJ132T2 | 17.1634 | PVBJ132 132.00 | T2 | PVBJ132 | PVBJ132T2 | 17.1634 | 88179
[12 empty] | 88107 | SCTY132 132.00 | T1 | SCTY132 | SCTY132T1 | 17.1303 | SCTY132 132.00 | T1 | SCTY132 | SCTY132T1 | 17.1303 | 88107
[12 empty] | 88107 | SCTY132 132.00 | T2 | SCTY132 | SCTY132T2 | 17.0774 | SCTY132 132.00 | T2 | SCTY132 | SCTY132T2 | 17.0774 | 88107
[12 empty] | 88173 | SDAM132 132.00 | T1 | SDAM132 | SDAM132T1 | 27.8943 | SDAM132 132.00 | T1 | SDAM132 | SDAM132T1 | 27.8943 | 88173
[12 empty] | 88173 | SDAM132 132.00 | T2 | SDAM132 | SDAM132T2 | 27.6488 | SDAM132 132.00 | T2 | SDAM132 | SDAM132T2 | 27.6488 | 88173
[12 empty] | 88122 | SGBT132 132.00 | T1 | SGBT132 | SGBT132T1 | 40.1111 | SGBT132 132.00 | T1 | SGBT132 | SGBT132T1 | 40.1111 | 88122
[12 empty] | 88122 | SGBT132 132.00 | T2 | SGBT132 | SGBT132T2 | 39.6472 | SGBT132 132.00 | T2 | SGBT132 | SGBT132T2 | 39.6472 | 88122
[12 empty] | 88142 | SHMS132 132.00 | T1 | SHMS132 | SHMS132T1 | 28.2235 | SHMS132 132.00 | T1 | SHMS132 | SHMS132T1 | 28.2235 | 88142
[12 empty] | 88142 | SHMS132 132.00 | T2 | SHMS132 | SHMS132T2 | 28.1138 | SHMS132 132.00 | T2 | SHMS132 | SHMS132T2 | 28.1138 | 88142
[12 empty] | 88132 | SMTN132 132.00 | T1 | SMTN132 | SMTN132T1 | 2.3382 | SMTN132 132.00 | T1 | SMTN132 | SMTN132T1 | 2.3382 | 88132
[12 empty] | 88132 | SMTN132 132.00 | T2 | SMTN132 | SMTN132T2 | 2.3527 | SMTN132 132.00 | T2 | SMTN132 | SMTN132T2 | 2.3527 | 88132
[12 empty] | 88162 | SPKC132 132.00 | T3 | SPKC132 | SPKC132T3 | 49.6522 | SPKC132 132.00 | T3 | SPKC132 | SPKC132T3 | 49.6522 | 88162
[12 empty] | 88162 | SPKC132 132.00 | T4 | SPKC132 | SPKC132T4 | 49.4036 | SPKC132 132.00 | T4 | SPKC132 | SPKC132T4 | 49.4036 | 88162
[12 empty] | 88162 | SPKC132 132.00 | T5 | SPKC132 | SPKC132T5 | 55.7688 | SPKC132 132.00 | T5 | SPKC132 | SPKC132T5 | 55.7688 | 88162
[12 empty] | 51050 | SRDN132 132.00 | T1 | SRDN132 | SRDN132T1 | 24.2483 | SRDN132 132.00 | T1 | SRDN132 | SRDN132T1 | 24.2483 | 51050
[12 empty] | 51050 | SRDN132 132.00 | T2 | SRDN132 | SRDN132T2 | 24.2006 | SRDN132 132.00 | T2 | SRDN132 | SRDN132T2 | 24.2006 | 51050
[12 empty] | 51130 | SRDR132 132.00 | T1 | SRDR132 | SRDR132T1 | 27.8539 | SRDR132 132.00 | T1 | SRDR132 | SRDR132T1 | 27.8539 | 51130
[12 empty] | 51130 | SRDR132 132.00 | T2 | SRDR132 | SRDR132T2 | 27.9781 | SRDR132 132.00 | T2 | SRDR132 | SRDR132T2 | 27.9781 | 51130
[12 empty] | 88118 | SRYA132 132.00 | T1 | SRYA132 | SRYA132T1 | 8.7137 | SRYA132 132.00 | T1 | SRYA132 | SRYA132T1 | 8.7137 | 88118
[12 empty] | 88118 | SRYA132 132.00 | T2 | SRYA132 | SRYA132T2 | 8.6619 | SRYA132 132.00 | T2 | SRYA132 | SRYA132T2 | 8.6619 | 88118
[12 empty] | 88118 | SRYA132 132.00 | T3 | SRYA132 | SRYA132T3 | 36.3325 | SRYA132 132.00 | T3 | SRYA132 | SRYA132T3 | 36.3325 | 88118
[12 empty] | 88118 | SRYA132 132.00 | T4 | SRYA132 | SRYA132T4 | 36.578 | SRYA132 132.00 | T4 | SRYA132 | SRYA132T4 | 36.578 | 88118
[12 empty] | 88127 | TMWT132 132.00 | T1 | TMWT132 | TMWT132T1 | 12.7439 | TMWT132 132.00 | T1 | TMWT132 | TMWT132T1 | 12.7439 | 88127
[12 empty] | 88127 | TMWT132 132.00 | T2 | TMWT132 | TMWT132T2 | 12.8433 | TMWT132 132.00 | T2 | TMWT132 | TMWT132T2 | 12.8433 | 88127
[12 empty] | 88134 | TNHQ132 132.00 | T1 | TNHQ132 | TNHQ132T1 | 22.9032 | TNHQ132 132.00 | T1 | TNHQ132 | TNHQ132T1 | 22.9032 | 88134
[12 empty] | 88134 | TNHQ132 132.00 | T2 | TNHQ132 | TNHQ132T2 | 23.0999 | TNHQ132 132.00 | T2 | TNHQ132 | TNHQ132T2 | 23.0999 | 88134
[12 empty] | 88137 | TWSA132 132.00 | T1 | TWSA132 | TWSA132T1 | 25.6452 | TWSA132 132.00 | T1 | TWSA132 | TWSA132T1 | 25.6452 | 88137
[12 empty] | 88137 | TWSA132 132.00 | T2 | TWSA132 | TWSA132T2 | 25.612 | TWSA132 132.00 | T2 | TWSA132 | TWSA132T2 | 25.612 | 88137
[12 empty] | 88160 | VCTY132 132.00 | T1 | VCTY132 | VCTY132T1 | 0 | VCTY132 132.00 | T1 | VCTY132 | VCTY132T1 | 0 | 88160
[12 empty] | 88160 | VCTY132 132.00 | T2 | VCTY132 | VCTY132T2 | 0 | VCTY132 132.00 | T2 | VCTY132 | VCTY132T2 | 0 | 88160
[12 empty] | 88160 | VCTY132 132.00 | T3 | VCTY132 | VCTY132T3 | 26.2675 | VCTY132 132.00 | T3 | VCTY132 | VCTY132T3 | 26.2675 | 88160
[12 empty] | 88160 | VCTY132 132.00 | T4 | VCTY132 | VCTY132T4 | 26.574 | VCTY132 132.00 | T4 | VCTY132 | VCTY132T4 | 26.574 | 88160
[12 empty] | 88159 | WMJU132 132.00 | T1 | WMJU132 | WMJU132T1 | 48.0243 | WMJU132 132.00 | T1 | WMJU132 | WMJU132T1 | 48.0243 | 88159
[12 empty] | 88159 | WMJU132 132.00 | T2 | WMJU132 | WMJU132T2 | 48.0855 | WMJU132 132.00 | T2 | WMJU132 | WMJU132T2 | 48.0855 | 88159
[12 empty] | 96152 | AMID132 132.00 | T1 | AMID132 | AMID132T1 | 6.7225 | AMID132 132.00 | T1 | AMID132 | AMID132T1 | 6.7225 | 96152
[12 empty] | 96152 | AMID132 132.00 | T2 | AMID132 | AMID132T2 | 7.4691 | AMID132 132.00 | T2 | AMID132 | AMID132T2 | 7.4691 | 96152
[12 empty] | 96152 | AMID132 132.00 | T3 | AMID132 | AMID132T3 | 31.9555 | AMID132 132.00 | T3 | AMID132 | AMID132T3 | 31.9555 | 96152
[12 empty] | 96152 | AMID132 132.00 | T4 | AMID132 | AMID132T4 | 31.6034 | AMID132 132.00 | T4 | AMID132 | AMID132T4 | 31.6034 | 96152
[12 empty] | 96138 | BAHA132 132.00 | T1 | BAHA132 | BAHA132T1 | 12.4001 | BAHA132 132.00 | T1 | BAHA132 | BAHA132T1 | 12.4001 | 96138
[12 empty] | 96138 | BAHA132 132.00 | T2 | BAHA132 | BAHA132T2 | 12.3835 | BAHA132 132.00 | T2 | BAHA132 | BAHA132T2 | 12.3835 | 96138
[12 empty] | 96138 | BAHA132 132.00 | T3 | BAHA132 | BAHA132T3 | 5.4177 | BAHA132 132.00 | T3 | BAHA132 | BAHA132T3 | 5.4177 | 96138
[12 empty] | 96138 | BAHA132 132.00 | T4 | BAHA132 | BAHA132T4 | 5.4674 | BAHA132 132.00 | T4 | BAHA132 | BAHA132T4 | 5.4674 | 96138
[12 empty] | 96146 | BBNL132 132.00 | T1 | BBNL132 | BBNL132T1 | 1.1059 | BBNL132 132.00 | T1 | BBNL132 | BBNL132T1 | 1.1059 | 96146
[12 empty] | 96146 | BBNL132 132.00 | T2 | BBNL132 | BBNL132T2 | 2.1 | BBNL132 132.00 | T2 | BBNL132 | BBNL132T2 | 2.1 | 96146
[12 empty] | 96192 | BKPY132 132.00 | T1 | BKPY132 | BKPY132T1 | 9.4189 | BKPY132 132.00 | T1 | BKPY132 | BKPY132T1 | 9.4189 | 96192
[12 empty] | 96192 | BKPY132 132.00 | T2 | BKPY132 | BKPY132T2 | 12.9096 | BKPY132 132.00 | T2 | BKPY132 | BKPY132T2 | 12.9096 | 96192
[12 empty] | 96176 | CMBG132 132.00 | T4 | CMBG132 | CMBG132T4 | 18.7322 | CMBG132 132.00 | T4 | CMBG132 | CMBG132T4 | 18.7322 | 96176
[12 empty] | 96140 | GMAS132 132.00 | T1 | GMAS132 | GMAS132T1 | 13.185 | GMAS132 132.00 | T1 | GMAS132 | GMAS132T1 | 13.185 | 96140
[12 empty] | 96140 | GMAS132 132.00 | T2 | GMAS132 | GMAS132T2 | 8.3409 | GMAS132 132.00 | T2 | GMAS132 | GMAS132T2 | 8.3409 | 96140
[12 empty] | 96112 | KKWG132 132.00 | T1 | KKWG132 | KKWG132T1 | 4.9932 | KKWG132 132.00 | T1 | KKWG132 | KKWG132T1 | 4.9932 | 96112
[12 empty] | 96112 | KKWG132 132.00 | T2 | KKWG132 | KKWG132T2 | 5.0066 | KKWG132 132.00 | T2 | KKWG132 | KKWG132T2 | 5.0066 | 96112
[12 empty] | 96132 | KLAT132 132.00 | T1 | KLAT132 | KLAT132T1 | 13.7411 | KLAT132 132.00 | T1 | KLAT132 | KLAT132T1 | 13.7411 | 96132
[12 empty] | 96132 | KLAT132 132.00 | T2 | KLAT132 | KLAT132T2 | 9.5856 | KLAT132 132.00 | T2 | KLAT132 | KLAT132T2 | 9.5856 | 96132
[12 empty] | 96137 | KPLH132 132.00 | T1 | KPLH132 | KPLH132T1 | 15.5283 | KPLH132 132.00 | T1 | KPLH132 | KPLH132T1 | 15.5283 | 96137
[12 empty] | 96137 | KPLH132 132.00 | T2 | KPLH132 | KPLH132T2 | 12.6579 | KPLH132 132.00 | T2 | KPLH132 | KPLH132T2 | 12.6579 | 96137
[12 empty] | 96134 | LKUT132 132.00 | T1 | LKUT132 | LKUT132T1 | 12.0335 | LKUT132 132.00 | T1 | LKUT132 | LKUT132T1 | 12.0335 | 96134
[12 empty] | 96134 | LKUT132 132.00 | T2 | LKUT132 | LKUT132T2 | 10 | LKUT132 132.00 | T2 | LKUT132 | LKUT132T2 | 10 | 96134
[12 empty] | 96134 | LKUT132 132.00 | T3 | LKUT132 | LKUT132T3 | 14.0103 | LKUT132 132.00 | T3 | LKUT132 | LKUT132T3 | 14.0103 | 96134
[12 empty] | 96134 | LKUT132 132.00 | T4 | LKUT132 | LKUT132T4 | 14.0621 | LKUT132 132.00 | T4 | LKUT132 | LKUT132T4 | 14.0621 | 96134
[12 empty] | 96156 | MTIN132 132.00 | T3 | MTIN132 | MTIN132T3 | 0 | MTIN132 132.00 | T3 | MTIN132 | MTIN132T3 | 0 | 96156
[12 empty] | 96156 | MTIN132 132.00 | T4 | MTIN132 | MTIN132T4 | 19.9934 | MTIN132 132.00 | T4 | MTIN132 | MTIN132T4 | 19.9934 | 96156
[12 empty] | 96125 | NLAI132 132.00 | T1 | NLAI132 | NLAI132T1 | 9.9377 | NLAI132 132.00 | T1 | NLAI132 | NLAI132T1 | 9.9377 | 96125
[12 empty] | 96125 | NLAI132 132.00 | T2 | NLAI132 | NLAI132T2 | 5.0035 | NLAI132 132.00 | T2 | NLAI132 | NLAI132T2 | 5.0035 | 96125
[12 empty] | 96136 | PBSR132 132.00 | T1 | PBSR132 | PBSR132T1 | 13.2223 | PBSR132 132.00 | T1 | PBSR132 | PBSR132T1 | 13.2223 | 96136
[12 empty] | 96136 | PBSR132 132.00 | T2 | PBSR132 | PBSR132T2 | 12.3825 | PBSR132 132.00 | T2 | PBSR132 | PBSR132T2 | 12.3825 | 96136
[12 empty] | 96188 | PJAM132 132.00 | T1 | PJAM132 | PJAM132T1 | 7.5716 | PJAM132 132.00 | T1 | PJAM132 | PJAM132T1 | 7.5716 | 96188
[12 empty] | 96188 | PJAM132 132.00 | T2 | PJAM132 | PJAM132T2 | 7.1501 | PJAM132 132.00 | T2 | PJAM132 | PJAM132T2 | 7.1501 | 96188
[12 empty] | 96188 | PJAM132 132.00 | T3 | PJAM132 | PJAM132T3 | 2.7751 | PJAM132 132.00 | T3 | PJAM132 | PJAM132T3 | 2.7751 | 96188
[12 empty] | 96188 | PJAM132 132.00 | T4 | PJAM132 | PJAM132T4 | 2.9615 | PJAM132 132.00 | T4 | PJAM132 | PJAM132T4 | 2.9615 | 96188
[12 empty] | 96158 | PROI132 132.00 | T1 | PROI132 | PROI132T1 | 12.2489 | PROI132 132.00 | T1 | PROI132 | PROI132T1 | 12.2489 | 96158
[12 empty] | 96158 | PROI132 132.00 | T2 | PROI132 | PROI132T2 | 15.4734 | PROI132 132.00 | T2 | PROI132 | PROI132T2 | 15.4734 | 96158
[12 empty] | 96158 | PROI132 132.00 | T3 | PROI132 | PROI132T3 | 27.2626 | PROI132 132.00 | T3 | PROI132 | PROI132T3 | 27.2626 | 96158
[12 empty] | 96158 | PROI132 132.00 | T4 | PROI132 | PROI132T4 | 27.3392 | PROI132 132.00 | T4 | PROI132 | PROI132T4 | 27.3392 | 96158
[12 empty] | 96117 | RASA132 132.00 | T1 | RASA132 | RASA132T1 | 9.685 | RASA132 132.00 | T1 | RASA132 | RASA132T1 | 9.685 | 96117
[12 empty] | 96117 | RASA132 132.00 | T2 | RASA132 | RASA132T2 | 9.6726 | RASA132 132.00 | T2 | RASA132 | RASA132T2 | 9.6726 | 96117
[12 empty] | 96142 | RTAU132 132.00 | T1 | RTAU132 | RTAU132T1 | 8.7707 | RTAU132 132.00 | T1 | RTAU132 | RTAU132T1 | 8.7707 | 96142
[12 empty] | 96142 | RTAU132 132.00 | T2 | RTAU132 | RTAU132T2 | 8.7727 | RTAU132 132.00 | T2 | RTAU132 | RTAU132T2 | 8.7727 | 96142
[12 empty] | 96149 | SBAN132 132.00 | T1 | SBAN132 | SBAN132T1 | 13.0193 | SBAN132 132.00 | T1 | SBAN132 | SBAN132T1 | 13.0193 | 96149
[12 empty] | 96149 | SBAN132 132.00 | T2 | SBAN132 | SBAN132T2 | 17.2773 | SBAN132 132.00 | T2 | SBAN132 | SBAN132T2 | 17.2773 | 96149
[12 empty] | 96150 | SDYN132 132.00 | T1 | SDYN132 | SDYN132T1 | 44.7532 | SDYN132 132.00 | T1 | SDYN132 | SDYN132T1 | 44.7532 | 96150
[12 empty] | 96150 | SDYN132 132.00 | T2 | SDYN132 | SDYN132T2 | 45.0318 | SDYN132 132.00 | T2 | SDYN132 | SDYN132T2 | 45.0318 | 96150
[12 empty] | 51079 | SLTI132 132.00 | T1 | SLTI132 | SLTI132T1 | 12.6455 | SLTI132 132.00 | T1 | SLTI132 | SLTI132T1 | 12.6455 | 51079
[12 empty] | 51079 | SLTI132 132.00 | T2 | SLTI132 | SLTI132T2 | 15.605 | SLTI132 132.00 | T2 | SLTI132 | SLTI132T2 | 15.605 | 51079
[12 empty] | 51079 | SLTI132 132.00 | T3 | SLTI132 | SLTI132T3 | 4.0281 | SLTI132 132.00 | T3 | SLTI132 | SLTI132T3 | 4.0281 | 51079
[12 empty] | 51079 | SLTI132 132.00 | T4 | SLTI132 | SLTI132T4 | 4.0281 | SLTI132 132.00 | T4 | SLTI132 | SLTI132T4 | 4.0281 | 51079
[12 empty] | 96133 | SMRK132 132.00 | T1 | SMRK132 | SMRK132T1 | 11.5406 | SMRK132 132.00 | T1 | SMRK132 | SMRK132T1 | 11.5406 | 96133
[12 empty] | 96133 | SMRK132 132.00 | T2 | SMRK132 | SMRK132T2 | 10.8013 | SMRK132 132.00 | T2 | SMRK132 | SMRK132T2 | 10.8013 | 96133
[12 empty] | 96143 | SNWG132 132.00 | T1 | SNWG132 | SNWG132T1 | 2.7027 | SNWG132 132.00 | T1 | SNWG132 | SNWG132T1 | 2.7027 | 96143
[12 empty] | 96143 | SNWG132 132.00 | T2 | SNWG132 | SNWG132T2 | 2.6923 | SNWG132 132.00 | T2 | SNWG132 | SNWG132T2 | 2.6923 | 96143
[12 empty] | 96139 | SPTG132 132.00 | T1 | SPTG132 | SPTG132T1 | 6.0276 | SPTG132 132.00 | T1 | SPTG132 | SPTG132T1 | 6.0276 | 96139
[12 empty] | 96139 | SPTG132 132.00 | T2 | SPTG132 | SPTG132T2 | 6.0991 | SPTG132 132.00 | T2 | SPTG132 | SPTG132T2 | 6.0991 | 96139
[12 empty] | 96139 | SPTG132 132.00 | T3 | SPTG132 | SPTG132T3 | 0 | SPTG132 132.00 | T3 | SPTG132 | SPTG132T3 | 0 | 96139
[12 empty] | 96139 | SPTG132 132.00 | T4 | SPTG132 | SPTG132T4 | 0 | SPTG132 132.00 | T4 | SPTG132 | SPTG132T4 | 0 | 96139
[12 empty] | 96190 | STRA132 132.00 | T1 | STRA132 | STRA132T1 | 13.0794 | STRA132 132.00 | T1 | STRA132 | STRA132T1 | 13.0794 | 96190
[12 empty] | 96190 | STRA132 132.00 | T2 | STRA132 | STRA132T2 | 6.9969 | STRA132 132.00 | T2 | STRA132 | STRA132T2 | 6.9969 | 96190
[12 empty] | 96131 | TJGS132 132.00 | T1 | TJGS132 | TJGS132T1 | 11.1792 | TJGS132 132.00 | T1 | TJGS132 | TJGS132T1 | 11.1792 | 96131
[12 empty] | 96131 | TJGS132 132.00 | T2 | TJGS132 | TJGS132T2 | 11.4112 | TJGS132 132.00 | T2 | TJGS132 | TJGS132T2 | 11.4112 | 96131
[12 empty] | 96915 | TJGSGT2A 15.750 | X1 | TJGSGT2 | TJGSGT2X1 | 0 | TJGSGT2A 15.750 | X1 | TJGSGT2 | TJGSGT2X1 | 0 | 96915
[12 empty] | 96135 | TJID132 132.00 | T1 | TJID132 | TJID132T1 | 11.1275 | TJID132 132.00 | T1 | TJID132 | TJID132T1 | 11.1275 | 96135
[12 empty] | 96135 | TJID132 132.00 | T2 | TJID132 | TJID132T2 | 7.8615 | TJID132 132.00 | T2 | TJID132 | TJID132T2 | 7.8615 | 96135
[12 empty] | 96135 | TJID132 132.00 | T3 | TJID132 | TJID132T3 | 19.9675 | TJID132 132.00 | T3 | TJID132 | TJID132T3 | 19.9675 | 96135
[12 empty] | 96135 | TJID132 132.00 | T4 | TJID132 | TJID132T4 | 19.9893 | TJID132 132.00 | T4 | TJID132 | TJID132T4 | 19.9893 | 96135
[12 empty] | 96144 | TKMG132 132.00 | T1 | TKMG132 | TKMG132T1 | 6.8529 | TKMG132 132.00 | T1 | TKMG132 | TKMG132T1 | 6.8529 | 96144
[12 empty] | 96144 | TKMG132 132.00 | T2 | TKMG132 | TKMG132T2 | 6.827 | TKMG132 132.00 | T2 | TKMG132 | TKMG132T2 | 6.827 | 96144
[12 empty] | 96129 | TTJF132 132.00 | T1 | TTJF132 | TTJF132T1 | 14.8677 | TTJF132 132.00 | T1 | TTJF132 | TTJF132T1 | 14.8677 | 96129
[12 empty] | 96129 | TTJF132 132.00 | T2 | TTJF132 | TTJF132T2 | 14.9029 | TTJF132 132.00 | T2 | TTJF132 | TTJF132T2 | 14.9029 | 96129
[12 empty] | 96165 | AFMS132 132.00 | T1 | AFMS132 | AFMS132T1 | 5.1319 | AFMS132 132.00 | T1 | AFMS132 | AFMS132T1 | 5.1319 | 96165
[12 empty] | 96165 | AFMS132 132.00 | T2 | AFMS132 | AFMS132T2 | 8.0852 | AFMS132 132.00 | T2 | AFMS132 | AFMS132T2 | 8.0852 | 96165
[12 empty] | 96105 | AKRH132 132.00 | T1 | AKRH132 | AKRH132T1 | 12.1278 | AKRH132 132.00 | T1 | AKRH132 | AKRH132T1 | 12.1278 | 96105
[12 empty] | 96105 | AKRH132 132.00 | T2 | AKRH132 | AKRH132T2 | 8.5356 | AKRH132 132.00 | T2 | AKRH132 | AKRH132T2 | 8.5356 | 96105
[12 empty] | 96107 | BBDM132 132.00 | T1 | BBDM132 | BBDM132T1 | 13.9616 | BBDM132 132.00 | T1 | BBDM132 | BBDM132T1 | 13.9616 | 96107
[12 empty] | 96107 | BBDM132 132.00 | T2 | BBDM132 | BBDM132T2 | 14.7621 | BBDM132 132.00 | T2 | BBDM132 | BBDM132T2 | 14.7621 | 96107
[12 empty] | 96107 | BBDM132 132.00 | T3 | BBDM132 | BBDM132T3 | 9.4261 | BBDM132 132.00 | T3 | BBDM132 | BBDM132T3 | 9.4261 | 96107
[12 empty] | 96107 | BBDM132 132.00 | T4 | BBDM132 | BBDM132T4 | 7.3272 | BBDM132 132.00 | T4 | BBDM132 | BBDM132T4 | 7.3272 | 96107
[12 empty] | 96111 | BMKA132 132.00 | T1 | BMKA132 | BMKA132T1 | 5.6828 | BMKA132 132.00 | T1 | BMKA132 | BMKA132T1 | 5.6828 | 96111
[12 empty] | 96111 | BMKA132 132.00 | T2 | BMKA132 | BMKA132T2 | 8.8483 | BMKA132 132.00 | T2 | BMKA132 | BMKA132T2 | 8.8483 | 96111
[12 empty] | 96101 | BRBI132 132.00 | T1 | BRBI132 | BRBI132T1 | 6.6624 | BRBI132 132.00 | T1 | BRBI132 | BRBI132T1 | 6.6624 | 96101
[12 empty] | 96101 | BRBI132 132.00 | T2 | BRBI132 | BRBI132T2 | 9.1227 | BRBI132 132.00 | T2 | BRBI132 | BRBI132T2 | 9.1227 | 96101
[12 empty] | 96101 | BRBI132 132.00 | T3 | BRBI132 | BRBI132T3 | 10.1531 | BRBI132 132.00 | T3 | BRBI132 | BRBI132T3 | 10.1531 | 96101
[12 empty] | 96101 | BRBI132 132.00 | T4 | BRBI132 | BRBI132T4 | 10.1313 | BRBI132 132.00 | T4 | BRBI132 | BRBI132T4 | 10.1313 | 96101
[12 empty] | 96122 | BVTA132 132.00 | T1 | BVTA132 | BVTA132T1 | 3.3695 | BVTA132 132.00 | T1 | BVTA132 | BVTA132T1 | 3.3695 | 96122
[12 empty] | 96122 | BVTA132 132.00 | T2 | BVTA132 | BVTA132T2 | 8.5501 | BVTA132 132.00 | T2 | BVTA132 | BVTA132T2 | 8.5501 | 96122
[12 empty] | 96191 | CHNG132 132.00 | T1 | CHNG132 | CHNG132T1 | 7.3438 | CHNG132 132.00 | T1 | CHNG132 | CHNG132T1 | 7.3438 | 96191
[12 empty] | 96191 | CHNG132 132.00 | T2 | CHNG132 | CHNG132T2 | 10.6045 | CHNG132 132.00 | T2 | CHNG132 | CHNG132T2 | 10.6045 | 96191
[12 empty] | 96191 | CHNG132 132.00 | T3 | CHNG132 | CHNG132T3 | 31.8406 | CHNG132 132.00 | T3 | CHNG132 | CHNG132T3 | 31.8406 | 96191
[12 empty] | 96191 | CHNG132 132.00 | T4 | CHNG132 | CHNG132T4 | 31.8509 | CHNG132 132.00 | T4 | CHNG132 | CHNG132T4 | 31.8509 | 96191
[12 empty] | 96921 | EMPP_GT1 24.000 | X1 | EMPP_GT | EMPP_GTX1 | 0 | EMPP_GT1 24.000 | X1 | EMPP_GT | EMPP_GTX1 | 0 | 96921
[12 empty] | 96922 | EMPP_GT2 24.000 | X1 | EMPP_GT | EMPP_GTX1 | 0 | EMPP_GT2 24.000 | X1 | EMPP_GT | EMPP_GTX1 | 0 | 96922
[12 empty] | 96923 | EMPP_GT3 24.000 | X1 | EMPP_GT | EMPP_GTX1 | 0 | EMPP_GT3 24.000 | X1 | EMPP_GT | EMPP_GTX1 | 0 | 96923
[12 empty] | 96106 | HPGH132 132.00 | T1 | HPGH132 | HPGH132T1 | 5.9893 | HPGH132 132.00 | T1 | HPGH132 | HPGH132T1 | 5.9893 | 96106
[12 empty] | 96106 | HPGH132 132.00 | T2 | HPGH132 | HPGH132T2 | 6.0111 | HPGH132 132.00 | T2 | HPGH132 | HPGH132T2 | 6.0111 | 96106
[12 empty] | 96109 | JSIN132 132.00 | T1 | JSIN132 | JSIN132T1 | 6.1726 | JSIN132 132.00 | T1 | JSIN132 | JSIN132T1 | 6.1726 | 96109
[12 empty] | 96109 | JSIN132 132.00 | T2 | JSIN132 | JSIN132T2 | 11.8078 | JSIN132 132.00 | T2 | JSIN132 | JSIN132T2 | 11.8078 | 96109
[12 empty] | 96109 | JSIN132 132.00 | T3 | JSIN132 | JSIN132T3 | 8.6236 | JSIN132 132.00 | T3 | JSIN132 | JSIN132T3 | 8.6236 | 96109
[12 empty] | 96109 | JSIN132 132.00 | T4 | JSIN132 | JSIN132T4 | 8.7034 | JSIN132 132.00 | T4 | JSIN132 | JSIN132T4 | 8.7034 | 96109
[12 empty] | 96118 | KGDK132 132.00 | T1 | KGDK132 | KGDK132T1 | 0 | KGDK132 132.00 | T1 | KGDK132 | KGDK132T1 | 0 | 96118
[12 empty] | 96118 | KGDK132 132.00 | T2 | KGDK132 | KGDK132T2 | 7.7973 | KGDK132 132.00 | T2 | KGDK132 | KGDK132T2 | 7.7973 | 96118
[12 empty] | 96126 | KLMK132 132.00 | T1 | KLMK132 | KLMK132T1 | 9.7606 | KLMK132 132.00 | T1 | KLMK132 | KLMK132T1 | 9.7606 | 96126
[12 empty] | 96126 | KLMK132 132.00 | T2 | KLMK132 | KLMK132T2 | 8.0769 | KLMK132 132.00 | T2 | KLMK132 | KLMK132T2 | 8.0769 | 96126
[12 empty] | 96126 | KLMK132 132.00 | T3 | KLMK132 | KLMK132T3 | 2.5991 | KLMK132 132.00 | T3 | KLMK132 | KLMK132T3 | 2.5991 | 96126
[12 empty] | 96126 | KLMK132 132.00 | T4 | KLMK132 | KLMK132T4 | 2.6302 | KLMK132 132.00 | T4 | KLMK132 | KLMK132T4 | 2.6302 | 96126
[12 empty] | 96102 | KRPH132 132.00 | T1 | KRPH132 | KRPH132T1 | 10.5963 | KRPH132 132.00 | T1 | KRPH132 | KRPH132T1 | 10.5963 | 96102
[12 empty] | 96102 | KRPH132 132.00 | T2 | KRPH132 | KRPH132T2 | 11.9973 | KRPH132 132.00 | T2 | KRPH132 | KRPH132T2 | 11.9973 | 96102
[12 empty] | 96405 | MCOP132 132.00 | T1 | MCOP132 | MCOP132T1 | 13.2057 | MCOP132 132.00 | T1 | MCOP132 | MCOP132T1 | 13.2057 | 96405
[12 empty] | 96405 | MCOP132 132.00 | T2 | MCOP132 | MCOP132T2 | 10.4834 | MCOP132 132.00 | T2 | MCOP132 | MCOP132T2 | 10.4834 | 96405
[12 empty] | 96405 | MCOP132 132.00 | T3 | MCOP132 | MCOP132T3 | 37.6735 | MCOP132 132.00 | T3 | MCOP132 | MCOP132T3 | 37.6735 | 96405
[12 empty] | 96405 | MCOP132 132.00 | T4 | MCOP132 | MCOP132T4 | 37.7336 | MCOP132 132.00 | T4 | MCOP132 | MCOP132T4 | 37.7336 | 96405
[12 empty] | 96198 | MFDR132 132.00 | F1 | MFDR132 | MFDR132F1 | 0 | MFDR132 132.00 | F1 | MFDR132 | MFDR132F1 | 0 | 96198
[12 empty] | 96120 | MJYA132 132.00 | T1 | MJYA132 | MJYA132T1 | 5.6155 | MJYA132 132.00 | T1 | MJYA132 | MJYA132T1 | 5.6155 | 96120
[12 empty] | 96120 | MJYA132 132.00 | T2 | MJYA132 | MJYA132T2 | 16.3764 | MJYA132 132.00 | T2 | MJYA132 | MJYA132T2 | 16.3764 | 96120
[12 empty] | 96121 | MMAU132 132.00 | T1 | MMAU132 | MMAU132T1 | 12.2479 | MMAU132 132.00 | T1 | MMAU132 | MMAU132T1 | 12.2479 | 96121
[12 empty] | 96121 | MMAU132 132.00 | T2 | MMAU132 | MMAU132T2 | 10.8727 | MMAU132 132.00 | T2 | MMAU132 | MMAU132T2 | 10.8727 | 96121
[12 empty] | 96108 | MMKA132 132.00 | T1 | MMKA132 | MMKA132T1 | 9.3723 | MMKA132 132.00 | T1 | MMKA132 | MMKA132T1 | 9.3723 | 96108
[12 empty] | 96108 | MMKA132 132.00 | T2 | MMKA132 | MMKA132T2 | 7.0093 | MMKA132 132.00 | T2 | MMKA132 | MMKA132T2 | 7.0093 | 96108
[12 empty] | 96177 | MPSS132 132.00 | T1 | MPSS132 | MPSS132T1 | 2.9429 | MPSS132 132.00 | T1 | MPSS132 | MPSS132T1 | 2.9429 | 96177
[12 empty] | 96177 | MPSS132 132.00 | T2 | MPSS132 | MPSS132T2 | 6.0121 | MPSS132 132.00 | T2 | MPSS132 | MPSS132T2 | 6.0121 | 96177
[12 empty] | 96173 | MTNH132 132.00 | T1 | MTNH132 | MTNH132T1 | 6.2285 | MTNH132 132.00 | T1 | MTNH132 | MTNH132T1 | 6.2285 | 96173
[12 empty] | 96173 | MTNH132 132.00 | T2 | MTNH132 | MTNH132T2 | 6.2451 | MTNH132 132.00 | T2 | MTNH132 | MTNH132T2 | 6.2451 | 96173
[12 empty] | 96173 | MTNH132 132.00 | T3 | MTNH132 | MTNH132T3 | 2.8093 | MTNH132 132.00 | T3 | MTNH132 | MTNH132T3 | 2.8093 | 96173
[12 empty] | 96173 | MTNH132 132.00 | T5 | MTNH132 | MTNH132T5 | 11.3801 | MTNH132 132.00 | T5 | MTNH132 | MTNH132T5 | 11.3801 | 96173
[12 empty] | 96173 | MTNH132 132.00 | T6 | MTNH132 | MTNH132T6 | 11.4733 | MTNH132 132.00 | T6 | MTNH132 | MTNH132T6 | 11.4733 | 96173
[12 empty] | 196105 | OZNA132 132.00 | T1 | OZNA132 | OZNA132T1 | 8.5563 | OZNA132 132.00 | T1 | OZNA132 | OZNA132T1 | 8.5563 | 196105
[12 empty] | 196105 | OZNA132 132.00 | T2 | OZNA132 | OZNA132T2 | 8.5563 | OZNA132 132.00 | T2 | OZNA132 | OZNA132T2 | 8.5563 | 196105
[12 empty] | 96123 | PGAD132 132.00 | T1 | PGAD132 | PGAD132T1 | 20.8052 | PGAD132 132.00 | T1 | PGAD132 | PGAD132T1 | 20.8052 | 96123
[12 empty] | 96123 | PGAD132 132.00 | T2 | PGAD132 | PGAD132T2 | 20.886 | PGAD132 132.00 | T2 | PGAD132 | PGAD132T2 | 20.886 | 96123
[12 empty] | 96147 | PPJG132 132.00 | T1 | PPJG132 | PPJG132T1 | 0 | PPJG132 132.00 | T1 | PPJG132 | PPJG132T1 | 0 | 96147
[12 empty] | 96147 | PPJG132 132.00 | T2 | PPJG132 | PPJG132T2 | 10.589 | PPJG132 132.00 | T2 | PPJG132 | PPJG132T2 | 10.589 | 96147
[12 empty] | 96189 | TGBU132 132.00 | T1 | TGBU132 | TGBU132T1 | 3.7268 | TGBU132 132.00 | T1 | TGBU132 | TGBU132T1 | 3.7268 | 96189
[12 empty] | 96189 | TGBU132 132.00 | T2 | TGBU132 | TGBU132T2 | 3.6387 | TGBU132 132.00 | T2 | TGBU132 | TGBU132T2 | 3.6387 | 96189
[12 empty] | 96189 | TGBU132 132.00 | T3 | TGBU132 | TGBU132T3 | 16.7823 | TGBU132 132.00 | T3 | TGBU132 | TGBU132T3 | 16.7823 | 96189
[12 empty] | 96189 | TGBU132 132.00 | T4 | TGBU132 | TGBU132T4 | 16.861 | TGBU132 132.00 | T4 | TGBU132 | TGBU132T4 | 16.861 | 96189
[12 empty] | 97117 | TKID132 132.00 | T1 | TKID132 | TKID132T1 | 8.4725 | TKID132 132.00 | T1 | TKID132 | TKID132T1 | 8.4725 | 97117
[12 empty] | 97117 | TKID132 132.00 | T2 | TKID132 | TKID132T2 | 8.3958 | TKID132 132.00 | T2 | TKID132 | TKID132T2 | 8.3958 | 97117
[12 empty] | 96110 | TMAS132 132.00 | T1 | TMAS132 | TMAS132T1 | 12.9779 | TMAS132 132.00 | T1 | TMAS132 | TMAS132T1 | 12.9779 | 96110
[12 empty] | 96110 | TMAS132 132.00 | T2 | TMAS132 | TMAS132T2 | 15.1711 | TMAS132 132.00 | T2 | TMAS132 | TMAS132T2 | 15.1711 | 96110
[12 empty] | 96113 | UPSR132 132.00 | T1 | UPSR132 | UPSR132T1 | 7.2423 | UPSR132 132.00 | T1 | UPSR132 | UPSR132T1 | 7.2423 | 96113
[12 empty] | 96113 | UPSR132 132.00 | T2 | UPSR132 | UPSR132T2 | 11.6318 | UPSR132 132.00 | T2 | UPSR132 | UPSR132T2 | 11.6318 | 96113
[12 empty] | 96113 | UPSR132 132.00 | T3 | UPSR132 | UPSR132T3 | 25.6545 | UPSR132 132.00 | T3 | UPSR132 | UPSR132T3 | 25.6545 | 96113
[12 empty] | 96113 | UPSR132 132.00 | T4 | UPSR132 | UPSR132T4 | 25.6421 | UPSR132 132.00 | T4 | UPSR132 | UPSR132T4 | 25.6421 | 96113
[12 empty] | 96195 | ZRNA132 132.00 | T1 | ZRNA132 | ZRNA132T1 | 6.7297 | ZRNA132 132.00 | T1 | ZRNA132 | ZRNA132T1 | 6.7297 | 96195
[12 empty] | 96195 | ZRNA132 132.00 | T2 | ZRNA132 | ZRNA132T2 | 6.7473 | ZRNA132 132.00 | T2 | ZRNA132 | ZRNA132T2 | 6.7473 | 96195
[12 empty] | 97122 | AHMJ132 132.00 | T1 | AHMJ132 | AHMJ132T1 | 12.0325 | AHMJ132 132.00 | T1 | AHMJ132 | AHMJ132T1 | 12.0325 | 97122
[12 empty] | 97122 | AHMJ132 132.00 | T2 | AHMJ132 | AHMJ132T2 | 12.1681 | AHMJ132 132.00 | T2 | AHMJ132 | AHMJ132T2 | 12.1681 | 97122
[12 empty] | 97164 | BBTU132 132.00 | T1 | BBTU132 | BBTU132T1 | 12.747 | BBTU132 132.00 | T1 | BBTU132 | BBTU132T1 | 12.747 | 97164
[12 empty] | 97164 | BBTU132 132.00 | T2 | BBTU132 | BBTU132T2 | 11.6597 | BBTU132 132.00 | T2 | BBTU132 | BBTU132T2 | 11.6597 | 97164
[12 empty] | 297111 | BBTU132_T7 132.00 | T7 | BBTU132 | BBTU132T7 | 8.5056 | BBTU132_T7 132.00 | T7 | BBTU132 | BBTU132T7 | 8.5056 | 297111
[12 empty] | 97174 | BKPG132 132.00 | T1 | BKPG132 | BKPG132T1 | 3.8365 | BKPG132 132.00 | T1 | BKPG132 | BKPG132T1 | 3.8365 | 97174
[12 empty] | 97174 | BKPG132 132.00 | T2 | BKPG132 | BKPG132T2 | 3.8427 | BKPG132 132.00 | T2 | BKPG132 | BKPG132T2 | 3.8427 | 97174
[12 empty] | 97102 | BKRI132 132.00 | T1 | BKRI132 | BKRI132T1 | 9.1735 | BKRI132 132.00 | T1 | BKRI132 | BKRI132T1 | 9.1735 | 97102
[12 empty] | 97102 | BKRI132 132.00 | T2 | BKRI132 | BKRI132T2 | 9.6757 | BKRI132 132.00 | T2 | BKRI132 | BKRI132T2 | 9.6757 | 97102
[12 empty] | 97106 | BPHE132 132.00 | T1 | BPHE132 | BPHE132T1 | 34.9874 | BPHE132 132.00 | T1 | BPHE132 | BPHE132T1 | 34.9874 | 97106
[12 empty] | 97106 | BPHE132 132.00 | T2 | BPHE132 | BPHE132T2 | 34.8942 | BPHE132 132.00 | T2 | BPHE132 | BPHE132T2 | 34.8942 | 97106
[12 empty] | 97129 | BPHT132 132.00 | T1 | BPHT132 | BPHT132T1 | 11.055 | BPHT132 132.00 | T1 | BPHT132 | BPHT132T1 | 11.055 | 97129
[12 empty] | 97129 | BPHT132 132.00 | T2 | BPHT132 | BPHT132T2 | 11.8906 | BPHT132 132.00 | T2 | BPHT132 | BPHT132T2 | 11.8906 | 97129
[12 empty] | 97182 | BSPT132 132.00 | T1 | BSPT132 | BSPT132T1 | 9.7761 | BSPT132 132.00 | T1 | BSPT132 | BSPT132T1 | 9.7761 | 97182
[12 empty] | 97182 | BSPT132 132.00 | T2 | BSPT132 | BSPT132T2 | 9.7906 | BSPT132 132.00 | T2 | BSPT132 | BSPT132T2 | 9.7906 | 97182
[12 empty] | 97182 | BSPT132 132.00 | T3 | BSPT132 | BSPT132T3 | 15.3606 | BSPT132 132.00 | T3 | BSPT132 | BSPT132T3 | 15.3606 | 97182
[12 empty] | 97182 | BSPT132 132.00 | T4 | BSPT132 | BSPT132T4 | 15.5418 | BSPT132 132.00 | T4 | BSPT132 | BSPT132T4 | 15.5418 | 97182
[12 empty] | 97148 | CAAH132 132.00 | T3 | CAAH132 | CAAH132T3 | 9.9708 | CAAH132 132.00 | T3 | CAAH132 | CAAH132T3 | 9.9708 | 97148
[12 empty] | 97148 | CAAH132 132.00 | T4 | CAAH132 | CAAH132T4 | 9.9108 | CAAH132 132.00 | T4 | CAAH132 | CAAH132T4 | 9.9108 | 97148
[12 empty] | 97178 | CBRU132 132.00 | T1 | CBRU132 | CBRU132T1 | 8.9871 | CBRU132 132.00 | T1 | CBRU132 | CBRU132T1 | 8.9871 | 97178
[12 empty] | 97178 | CBRU132 132.00 | T2 | CBRU132 | CBRU132T2 | 8.9519 | CBRU132 132.00 | T2 | CBRU132 | CBRU132T2 | 8.9519 | 97178
[12 empty] | 97178 | CBRU132 132.00 | T3 | CBRU132 | CBRU132T3 | 24.7029 | CBRU132 132.00 | T3 | CBRU132 | CBRU132T3 | 24.7029 | 97178
[12 empty] | 97178 | CBRU132 132.00 | T4 | CBRU132 | CBRU132T4 | 24.4833 | CBRU132 132.00 | T4 | CBRU132 | CBRU132T4 | 24.4833 | 97178
[12 empty] | 97197 | DBAY132 132.00 | T1 | DBAY132 | DBAY132T1 | 0 | DBAY132 132.00 | T1 | DBAY132 | DBAY132T1 | 0 | 97197
[12 empty] | 97197 | DBAY132 132.00 | T2 | DBAY132 | DBAY132T2 | 0 | DBAY132 132.00 | T2 | DBAY132 | DBAY132T2 | 0 | 97197
[12 empty] | 97157 | DSRU132 132.00 | T1 | DSRU132 | DSRU132T1 | 4.4941 | DSRU132 132.00 | T1 | DSRU132 | DSRU132T1 | 4.4941 | 97157
[12 empty] | 97157 | DSRU132 132.00 | T2 | DSRU132 | DSRU132T2 | 6.4636 | DSRU132 132.00 | T2 | DSRU132 | DSRU132T2 | 6.4636 | 97157
[12 empty] | 97176 | FCTR132 132.00 | T1 | FCTR132 | FCTR132T1 | 37.7853 | FCTR132 132.00 | T1 | FCTR132 | FCTR132T1 | 37.7853 | 97176
[12 empty] | 97176 | FCTR132 132.00 | T2 | FCTR132 | FCTR132T2 | 39.1211 | FCTR132 132.00 | T2 | FCTR132 | FCTR132T2 | 39.1211 | 97176
[12 empty] | 97187 | GPTH132 132.00 | T1 | GPTH132 | GPTH132T1 | 6.9482 | GPTH132 132.00 | T1 | GPTH132 | GPTH132T1 | 6.9482 | 97187
[12 empty] | 97187 | GPTH132 132.00 | T2 | GPTH132 | GPTH132T2 | 6.9182 | GPTH132 132.00 | T2 | GPTH132 | GPTH132T2 | 6.9182 | 97187
[12 empty] | 97187 | GPTH132 132.00 | T3 | GPTH132 | GPTH132T3 | 38.5133 | GPTH132 132.00 | T3 | GPTH132 | GPTH132T3 | 38.5133 | 97187
[12 empty] | 97187 | GPTH132 132.00 | T4 | GPTH132 | GPTH132T4 | 38.445 | GPTH132 132.00 | T4 | GPTH132 | GPTH132T4 | 38.445 | 97187
[12 empty] | 97105 | GRSK132 132.00 | T1 | GRSK132 | GRSK132T1 | 12.0087 | GRSK132 132.00 | T1 | GRSK132 | GRSK132T1 | 12.0087 | 97105
[12 empty] | 97105 | GRSK132 132.00 | T2 | GRSK132 | GRSK132T2 | 11.9807 | GRSK132 132.00 | T2 | GRSK132 | GRSK132T2 | 11.9807 | 97105
[12 empty] | 97253 | GSDC275 275.00 | T1 | GSDC275 | GSDC275T1 | 0 | GSDC275 275.00 | T1 | GSDC275 | GSDC275T1 | 0 | 97253
[12 empty] | 97253 | GSDC275 275.00 | T2 | GSDC275 | GSDC275T2 | 0 | GSDC275 275.00 | T2 | GSDC275 | GSDC275T2 | 0 | 97253
[12 empty] | 97253 | GSDC275 275.00 | T3 | GSDC275 | GSDC275T3 | 0 | GSDC275 275.00 | T3 | GSDC275 | GSDC275T3 | 0 | 97253
[12 empty] | 97253 | GSDC275 275.00 | T4 | GSDC275 | GSDC275T4 | 0 | GSDC275 275.00 | T4 | GSDC275 | GSDC275T4 | 0 | 97253
[12 empty] | 97407 | GWDC132 132.00 | T1 | GWDC132 | GWDC132T1 | 30.3815 | GWDC132 132.00 | T1 | GWDC132 | GWDC132T1 | 30.3815 | 97407
[12 empty] | 97407 | GWDC132 132.00 | T2 | GWDC132 | GWDC132T2 | 27.8963 | GWDC132 132.00 | T2 | GWDC132 | GWDC132T2 | 27.8963 | 97407
[12 empty] | 97194 | JBSK132 132.00 | T1 | JBSK132 | JBSK132T1 | 25.7425 | JBSK132 132.00 | T1 | JBSK132 | JBSK132T1 | 25.7425 | 97194
[12 empty] | 97194 | JBSK132 132.00 | T2 | JBSK132 | JBSK132T2 | 25.2548 | JBSK132 132.00 | T2 | JBSK132 | JBSK132T2 | 25.2548 | 97194
[12 empty] | 97150 | JMTH132 132.00 | T1 | JMTH132 | JMTH132T1 | 6.389 | JMTH132 132.00 | T1 | JMTH132 | JMTH132T1 | 6.389 | 97150
[12 empty] | 97150 | JMTH132 132.00 | T2 | JMTH132 | JMTH132T2 | 7.5384 | JMTH132 132.00 | T2 | JMTH132 | JMTH132T2 | 7.5384 | 97150
[12 empty] | 97110 | JTGH132 132.00 | T1 | JTGH132 | JTGH132T1 | 12.193 | JTGH132 132.00 | T1 | JTGH132 | JTGH132T1 | 12.193 | 97110
[12 empty] | 97110 | JTGH132 132.00 | T2 | JTGH132 | JTGH132T2 | 12.2458 | JTGH132 132.00 | T2 | JTGH132 | JTGH132T2 | 12.2458 | 97110
[12 empty] | 97173 | KBEK132 132.00 | T1 | KBEK132 | KBEK132T1 | 0.232 | KBEK132 132.00 | T1 | KBEK132 | KBEK132T1 | 0.232 | 97173
[12 empty] | 97173 | KBEK132 132.00 | T2 | KBEK132 | KBEK132T2 | 0.8232 | KBEK132 132.00 | T2 | KBEK132 | KBEK132T2 | 0.8232 | 97173
[12 empty] | 97168 | KKUP132 132.00 | T1 | KKUP132 | KKUP132T1 | 2.6664 | KKUP132 132.00 | T1 | KKUP132 | KKUP132T1 | 2.6664 | 97168
[12 empty] | 97168 | KKUP132 132.00 | T2 | KKUP132 | KKUP132T2 | 4.6753 | KKUP132 132.00 | T2 | KKUP132 | KKUP132T2 | 4.6753 | 97168
[12 empty] | 97112 | KLAI132 132.00 | T1 | KLAI132 | KLAI132T1 | 0 | KLAI132 132.00 | T1 | KLAI132 | KLAI132T1 | 0 | 97112
[12 empty] | 597112 | KLAI132R 132.00 | T2 | KLAI132R | KLAI132RT2 | 20.1353 | KLAI132R 132.00 | T2 | KLAI132R | KLAI132RT2 | 20.1353 | 597112
[12 empty] | 97149 | KLID132 132.00 | T1 | KLID132 | KLID132T1 | 10.1261 | KLID132 132.00 | T1 | KLID132 | KLID132T1 | 10.1261 | 97149
[12 empty] | 97149 | KLID132 132.00 | T2 | KLID132 | KLID132T2 | 10.852 | KLID132 132.00 | T2 | KLID132 | KLID132T2 | 10.852 | 97149
[12 empty] | 97149 | KLID132 132.00 | T3 | KLID132 | KLID132T3 | 6.3331 | KLID132 132.00 | T3 | KLID132 | KLID132T3 | 6.3331 | 97149
[12 empty] | 97149 | KLID132 132.00 | T4 | KLID132 | KLID132T4 | 10.1158 | KLID132 132.00 | T4 | KLID132 | KLID132T4 | 10.1158 | 97149
[12 empty] | 97109 | KLUG132 132.00 | T1 | KLUG132 | KLUG132T1 | 8.5646 | KLUG132 132.00 | T1 | KLUG132 | KLUG132T1 | 8.5646 | 97109
[12 empty] | 97109 | KLUG132 132.00 | T2 | KLUG132 | KLUG132T2 | 8.2529 | KLUG132 132.00 | T2 | KLUG132 | KLUG132T2 | 8.2529 | 97109
[12 empty] | 97109 | KLUG132 132.00 | T3 | KLUG132 | KLUG132T3 | 12.4208 | KLUG132 132.00 | T3 | KLUG132 | KLUG132T3 | 12.4208 | 97109
[12 empty] | 97109 | KLUG132 132.00 | T4 | KLUG132 | KLUG132T4 | 12.4125 | KLUG132 132.00 | T4 | KLUG132 | KLUG132T4 | 12.4125 | 97109
[12 empty] | 97132 | KPTR132 132.00 | T1 | KPTR132 | KPTR132T1 | 11.7539 | KPTR132 132.00 | T1 | KPTR132 | KPTR132T1 | 11.7539 | 97132
[12 empty] | 97132 | KPTR132 132.00 | T2 | KPTR132 | KPTR132T2 | 11.7488 | KPTR132 132.00 | T2 | KPTR132 | KPTR132T2 | 11.7488 | 97132
[12 empty] | 97158 | KSNI132 132.00 | F1 | KSNI132 | KSNI132F1 | 0 | KSNI132 132.00 | F1 | KSNI132 | KSNI132F1 | 0 | 97158
[12 empty] | 97158 | KSNI132 132.00 | F2 | KSNI132 | KSNI132F2 | 0 | KSNI132 132.00 | F2 | KSNI132 | KSNI132F2 | 0 | 97158
[12 empty] | 97189 | KTBR132 132.00 | T1 | KTBR132 | KTBR132T1 | 10.2173 | KTBR132 132.00 | T1 | KTBR132 | KTBR132T1 | 10.2173 | 97189
[12 empty] | 97189 | KTBR132 132.00 | T2 | KTBR132 | KTBR132T2 | 10.7071 | KTBR132 132.00 | T2 | KTBR132 | KTBR132T2 | 10.7071 | 97189
[12 empty] | 97189 | KTBR132 132.00 | T3 | KTBR132 | KTBR132T3 | 33.488 | KTBR132 132.00 | T3 | KTBR132 | KTBR132T3 | 33.488 | 97189
[12 empty] | 97189 | KTBR132 132.00 | T4 | KTBR132 | KTBR132T4 | 33.0324 | KTBR132 132.00 | T4 | KTBR132 | KTBR132T4 | 33.0324 | 97189
[12 empty] | 97189 | KTBR132 132.00 | T5 | KTBR132 | KTBR132T5 | 5.8599 | KTBR132 132.00 | T5 | KTBR132 | KTBR132T5 | 5.8599 | 97189
[12 empty] | 97189 | KTBR132 132.00 | T6 | KTBR132 | KTBR132T6 | 5.7791 | KTBR132 132.00 | T6 | KTBR132 | KTBR132T6 | 5.7791 | 97189
[12 empty] | 97249 | KTDC275 275.00 | T1 | KTDC275 | KTDC275T1 | 28.0517 | KTDC275 275.00 | T1 | KTDC275 | KTDC275T1 | 28.0517 | 97249
[12 empty] | 97249 | KTDC275 275.00 | T2 | KTDC275 | KTDC275T2 | 22.9052 | KTDC275 275.00 | T2 | KTDC275 | KTDC275T2 | 22.9052 | 97249
[12 empty] | 97116 | KTGI132 132.00 | T3 | KTGI132 | KTGI132T3 | 8.3233 | KTGI132 132.00 | T3 | KTGI132 | KTGI132T3 | 8.3233 | 97116
[12 empty] | 97116 | KTGI132 132.00 | T4 | KTGI132 | KTGI132T4 | 5.8112 | KTGI132 132.00 | T4 | KTGI132 | KTGI132T4 | 5.8112 | 97116
[12 empty] | 97185 | LKIN132 132.00 | T1 | LKIN132 | LKIN132T1 | 11.7415 | LKIN132 132.00 | T1 | LKIN132 | LKIN132T1 | 11.7415 | 97185
[12 empty] | 97185 | LKIN132 132.00 | T2 | LKIN132 | LKIN132T2 | 11.7995 | LKIN132 132.00 | T2 | LKIN132 | LKIN132T2 | 11.7995 | 97185
[12 empty] | 97185 | LKIN132 132.00 | T3 | LKIN132 | LKIN132T3 | 14.206 | LKIN132 132.00 | T3 | LKIN132 | LKIN132T3 | 14.206 | 97185
[12 empty] | 97185 | LKIN132 132.00 | T4 | LKIN132 | LKIN132T4 | 14.1263 | LKIN132 132.00 | T4 | LKIN132 | LKIN132T4 | 14.1263 | 97185
[12 empty] | 97115 | MAJD132 132.00 | T1 | MAJD132 | MAJD132T1 | 6.5547 | MAJD132 132.00 | T1 | MAJD132 | MAJD132T1 | 6.5547 | 97115
[12 empty] | 97115 | MAJD132 132.00 | T2 | MAJD132 | MAJD132T2 | 6.2513 | MAJD132 132.00 | T2 | MAJD132 | MAJD132T2 | 6.2513 | 97115
[12 empty] | 97140 | MKBL132 132.00 | T1 | MKBL132 | MKBL132T1 | 5.6528 | MKBL132 132.00 | T1 | MKBL132 | MKBL132T1 | 5.6528 | 97140
[12 empty] | 97140 | MKBL132 132.00 | T2 | MKBL132 | MKBL132T2 | 15.2519 | MKBL132 132.00 | T2 | MKBL132 | MKBL132T2 | 15.2519 | 97140
[12 empty] | 97136 | MSAI132 132.00 | T1 | MSAI132 | MSAI132T1 | 11.7995 | MSAI132 132.00 | T1 | MSAI132 | MSAI132T1 | 11.7995 | 97136
[12 empty] | 97136 | MSAI132 132.00 | T2 | MSAI132 | MSAI132T2 | 11.7798 | MSAI132 132.00 | T2 | MSAI132 | MSAI132T2 | 11.7798 | 97136
[12 empty] | 97131 | MSNG132 132.00 | T1 | MSNG132 | MSNG132T1 | 2.8311 | MSNG132 132.00 | T1 | MSNG132 | MSNG132T1 | 2.8311 | 97131
[12 empty] | 97131 | MSNG132 132.00 | T2 | MSNG132 | MSNG132T2 | 3.8686 | MSNG132 132.00 | T2 | MSNG132 | MSNG132T2 | 3.8686 | 97131
[12 empty] | 97131 | MSNG132 132.00 | T3 | MSNG132 | MSNG132T3 | 6.8384 | MSNG132 132.00 | T3 | MSNG132 | MSNG132T3 | 6.8384 | 97131
[12 empty] | 97131 | MSNG132 132.00 | T4 | MSNG132 | MSNG132T4 | 6.8291 | MSNG132 132.00 | T4 | MSNG132 | MSNG132T4 | 6.8291 | 97131
[12 empty] | 97147 | MUAR132 132.00 | T2 | MUAR132 | MUAR132T2 | 9.4168 | MUAR132 132.00 | T2 | MUAR132 | MUAR132T2 | 9.4168 | 97147
[12 empty] | 97147 | MUAR132 132.00 | T3 | MUAR132 | MUAR132T3 | 12.6041 | MUAR132 132.00 | T3 | MUAR132 | MUAR132T3 | 12.6041 | 97147
[12 empty] | 97138 | NYOR132 132.00 | T1 | NYOR132 | NYOR132T1 | 11.3926 | NYOR132 132.00 | T1 | NYOR132 | NYOR132T1 | 11.3926 | 97138
[12 empty] | 97138 | NYOR132 132.00 | T2 | NYOR132 | NYOR132T2 | 16.6104 | NYOR132 132.00 | T2 | NYOR132 | NYOR132T2 | 16.6104 | 97138
[12 empty] | 97177 | PBJB132 132.00 | T1 | PBJB132 | PBJB132T1 | 9.6229 | PBJB132 132.00 | T1 | PBJB132 | PBJB132T1 | 9.6229 | 97177
[12 empty] | 97177 | PBJB132 132.00 | T2 | PBJB132 | PBJB132T2 | 9.6198 | PBJB132 132.00 | T2 | PBJB132 | PBJB132T2 | 9.6198 | 97177
[12 empty] | 97177 | PBJB132 132.00 | T3 | PBJB132 | PBJB132T3 | 43.0716 | PBJB132 132.00 | T3 | PBJB132 | PBJB132T3 | 43.0716 | 97177
[12 empty] | 97177 | PBJB132 132.00 | T4 | PBJB132 | PBJB132T4 | 43.2466 | PBJB132 132.00 | T4 | PBJB132 | PBJB132T4 | 43.2466 | 97177
[12 empty] | 97244 | PCGP275 275.00 | 1 | PCGP275 | PCGP2751 | 0 | PCGP275 275.00 | 1 | PCGP275 | PCGP2751 | 0 | 97244
[12 empty] | 97153 | PGDT132 132.00 | T1 | PGDT132 | PGDT132T1 | 2.4873 | PGDT132 132.00 | T1 | PGDT132 | PGDT132T1 | 2.4873 | 97153
[12 empty] | 97153 | PGDT132 132.00 | T2 | PGDT132 | PGDT132T2 | 10.1427 | PGDT132 132.00 | T2 | PGDT132 | PGDT132T2 | 10.1427 | 97153
[12 empty] | 97153 | PGDT132 132.00 | T3 | PGDT132 | PGDT132T3 | 16.3681 | PGDT132 132.00 | T3 | PGDT132 | PGDT132T3 | 16.3681 | 97153
[12 empty] | 97153 | PGDT132 132.00 | T4 | PGDT132 | PGDT132T4 | 16.4624 | PGDT132 132.00 | T4 | PGDT132 | PGDT132T4 | 16.4624 | 97153
[12 empty] | 97191 | PGEH132 132.00 | T1 | PGEH132 | PGEH132T1 | 2.0379 | PGEH132 132.00 | T1 | PGEH132 | PGEH132T1 | 2.0379 | 97191
[12 empty] | 97191 | PGEH132 132.00 | T2 | PGEH132 | PGEH132T2 | 2.0275 | PGEH132 132.00 | T2 | PGEH132 | PGEH132T2 | 2.0275 | 97191
[12 empty] | 97123 | PGIE132 132.00 | T1 | PGIE132 | PGIE132T1 | 13.8622 | PGIE132 132.00 | T1 | PGIE132 | PGIE132T1 | 13.8622 | 97123
[12 empty] | 97123 | PGIE132 132.00 | T2 | PGIE132 | PGIE132T2 | 13.8715 | PGIE132 132.00 | T2 | PGIE132 | PGIE132T2 | 13.8715 | 97123
[12 empty] | 97123 | PGIE132 132.00 | T3 | PGIE132 | PGIE132T3 | 12.4343 | PGIE132 132.00 | T3 | PGIE132 | PGIE132T3 | 12.4343 | 97123
[12 empty] | 97179 | PGOH132 132.00 | T1 | PGOH132 | PGOH132T1 | 3.4762 | PGOH132 132.00 | T1 | PGOH132 | PGOH132T1 | 3.4762 | 97179
[12 empty] | 97179 | PGOH132 132.00 | T2 | PGOH132 | PGOH132T2 | 3.4658 | PGOH132 132.00 | T2 | PGOH132 | PGOH132T2 | 3.4658 | 97179
[12 empty] | 97114 | PGPS132 132.00 | N1 | PGPS132 | PGPS132N1 | 0 | PGPS132 132.00 | N1 | PGPS132 | PGPS132N1 | 0 | 97114
[12 empty] | 97114 | PGPS132 132.00 | N2 | PGPS132 | PGPS132N2 | 0 | PGPS132 132.00 | N2 | PGPS132 | PGPS132N2 | 0 | 97114
[12 empty] | 97114 | PGPS132 132.00 | T2 | PGPS132 | PGPS132T2 | 0 | PGPS132 132.00 | T2 | PGPS132 | PGPS132T2 | 0 | 97114
[12 empty] | 97167 | PGTC132 132.00 | T1 | PGTC132 | PGTC132T1 | 47.8349 | PGTC132 132.00 | T1 | PGTC132 | PGTC132T1 | 47.8349 | 97167
[12 empty] | 97167 | PGTC132 132.00 | T2 | PGTC132 | PGTC132T2 | 47.6754 | PGTC132 132.00 | T2 | PGTC132 | PGTC132T2 | 47.6754 | 97167
[12 empty] | 97103 | PJML132 132.00 | T3 | PJML132 | PJML132T3 | 9.6156 | PJML132 132.00 | T3 | PJML132 | PJML132T3 | 9.6156 | 97103
[12 empty] | 97103 | PJML132 132.00 | T4 | PJML132 | PJML132T4 | 9.5804 | PJML132 132.00 | T4 | PJML132 | PJML132T4 | 9.5804 | 97103
[12 empty] | 97198 | PLGI132 132.00 | T1 | PLGI132 | PLGI132T1 | 29.0561 | PLGI132 132.00 | T1 | PLGI132 | PLGI132T1 | 29.0561 | 97198
[12 empty] | 97198 | PLGI132 132.00 | T2 | PLGI132 | PLGI132T2 | 29.2052 | PLGI132 132.00 | T2 | PLGI132 | PLGI132T2 | 29.2052 | 97198
[12 empty] | 97108 | PLNG132 132.00 | T1 | PLNG132 | PLNG132T1 | 11.4568 | PLNG132 132.00 | T1 | PLNG132 | PLNG132T1 | 11.4568 | 97108
[12 empty] | 97108 | PLNG132 132.00 | T2 | PLNG132 | PLNG132T2 | 11.2983 | PLNG132 132.00 | T2 | PLNG132 | PLNG132T2 | 11.2983 | 97108
[12 empty] | 97108 | PLNG132 132.00 | T3 | PLNG132 | PLNG132T3 | 41.8124 | PLNG132 132.00 | T3 | PLNG132 | PLNG132T3 | 41.8124 | 97108
[12 empty] | 97108 | PLNG132 132.00 | T4 | PLNG132 | PLNG132T4 | 42.6677 | PLNG132 132.00 | T4 | PLNG132 | PLNG132T4 | 42.6677 | 97108
[12 empty] | 97165 | PMJY132 132.00 | T1 | PMJY132 | PMJY132T1 | 10.4844 | PMJY132 132.00 | T1 | PMJY132 | PMJY132T1 | 10.4844 | 97165
[12 empty] | 97165 | PMJY132 132.00 | T2 | PMJY132 | PMJY132T2 | 13.0918 | PMJY132 132.00 | T2 | PMJY132 | PMJY132T2 | 13.0918 | 97165
[12 empty] | 97165 | PMJY132 132.00 | T3 | PMJY132 | PMJY132T3 | 35.9556 | PMJY132 132.00 | T3 | PMJY132 | PMJY132T3 | 35.9556 | 97165
[12 empty] | 97165 | PMJY132 132.00 | T4 | PMJY132 | PMJY132T4 | 38.0297 | PMJY132 132.00 | T4 | PMJY132 | PMJY132T4 | 38.0297 | 97165
[12 empty] | 97155 | PNAS132 132.00 | T1 | PNAS132 | PNAS132T1 | 12.2686 | PNAS132 132.00 | T1 | PNAS132 | PNAS132T1 | 12.2686 | 97155
[12 empty] | 97155 | PNAS132 132.00 | T2 | PNAS132 | PNAS132T2 | 16.2076 | PNAS132 132.00 | T2 | PNAS132 | PNAS132T2 | 16.2076 | 97155
[12 empty] | 97145 | PNWR132 132.00 | T1 | PNWR132 | PNWR132T1 | 6.2544 | PNWR132 132.00 | T1 | PNWR132 | PNWR132T1 | 6.2544 | 97145
[12 empty] | 97145 | PNWR132 132.00 | T2 | PNWR132 | PNWR132T2 | 5.162 | PNWR132 132.00 | T2 | PNWR132 | PNWR132T2 | 5.162 | 97145
[12 empty] | 97151 | PONT132 132.00 | T1 | PONT132 | PONT132T1 | 6.5195 | PONT132 132.00 | T1 | PONT132 | PONT132T1 | 6.5195 | 97151
[12 empty] | 97151 | PONT132 132.00 | T2 | PONT132 | PONT132T2 | 11.2538 | PONT132 132.00 | T2 | PONT132 | PONT132T2 | 11.2538 | 97151
[12 empty] | 97151 | PONT132 132.00 | T3 | PONT132 | PONT132T3 | 12.456 | PONT132 132.00 | T3 | PONT132 | PONT132T3 | 12.456 | 97151
[12 empty] | 97151 | PONT132 132.00 | T4 | PONT132 | PONT132T4 | 12.4829 | PONT132 132.00 | T4 | PONT132 | PONT132T4 | 12.4829 | 97151
[12 empty] | 97119 | PRJA132 132.00 | T1 | PRJA132 | PRJA132T1 | 20.4677 | PRJA132 132.00 | T1 | PRJA132 | PRJA132T1 | 20.4677 | 97119
[12 empty] | 97119 | PRJA132 132.00 | T2 | PRJA132 | PRJA132T2 | 0 | PRJA132 132.00 | T2 | PRJA132 | PRJA132T2 | 0 | 97119
[12 empty] | 97119 | PRJA132 132.00 | T3 | PRJA132 | PRJA132T3 | 1.2457 | PRJA132 132.00 | T3 | PRJA132 | PRJA132T3 | 1.2457 | 97119
[12 empty] | 97119 | PRJA132 132.00 | T4 | PRJA132 | PRJA132T4 | 1.2571 | PRJA132 132.00 | T4 | PRJA132 | PRJA132T4 | 1.2571 | 97119
[12 empty] | 97163 | PSAK132 132.00 | T1 | PSAK132 | PSAK132T1 | 7.9858 | PSAK132 132.00 | T1 | PSAK132 | PSAK132T1 | 7.9858 | 97163
[12 empty] | 97163 | PSAK132 132.00 | T2 | PSAK132 | PSAK132T2 | 16.4748 | PSAK132 132.00 | T2 | PSAK132 | PSAK132T2 | 16.4748 | 97163
[12 empty] | 97163 | PSAK132 132.00 | T3 | PSAK132 | PSAK132T3 | 11.9331 | PSAK132 132.00 | T3 | PSAK132 | PSAK132T3 | 11.9331 | 97163
[12 empty] | 97163 | PSAK132 132.00 | T4 | PSAK132 | PSAK132T4 | 12.0263 | PSAK132 132.00 | T4 | PSAK132 | PSAK132T4 | 12.0263 | 97163
[12 empty] | 97181 | PSLG132 132.00 | T3 | PSLG132 | PSLG132T3 | 6.4667 | PSLG132 132.00 | T3 | PSLG132 | PSLG132T3 | 6.4667 | 97181
[12 empty] | 97181 | PSLG132 132.00 | T4 | PSLG132 | PSLG132T4 | 7.497 | PSLG132 132.00 | T4 | PSLG132 | PSLG132T4 | 7.497 | 97181
[12 empty] | 97120 | PSRI132 132.00 | T1 | PSRI132 | PSRI132T1 | 6.8032 | PSRI132 132.00 | T1 | PSRI132 | PSRI132T1 | 6.8032 | 97120
[12 empty] | 97120 | PSRI132 132.00 | T2 | PSRI132 | PSRI132T2 | 16.16 | PSRI132 132.00 | T2 | PSRI132 | PSRI132T2 | 16.16 | 97120
[12 empty] | 97118 | PUBB132 132.00 | T1 | PUBB132 | PUBB132T1 | 10.1582 | PUBB132 132.00 | T1 | PUBB132 | PUBB132T1 | 10.1582 | 97118
[12 empty] | 97118 | PUBB132 132.00 | T2 | PUBB132 | PUBB132T2 | 10.2514 | PUBB132 132.00 | T2 | PUBB132 | PUBB132T2 | 10.2514 | 97118
[12 empty] | 97104 | PYSF132 132.00 | T1 | PYSF132 | PYSF132T1 | 4.0208 | PYSF132 132.00 | T1 | PYSF132 | PYSF132T1 | 4.0208 | 97104
[12 empty] | 97104 | PYSF132 132.00 | T2 | PYSF132 | PYSF132T2 | 3.9867 | PYSF132 132.00 | T2 | PYSF132 | PYSF132T2 | 3.9867 | 97104
[12 empty] | 97111 | RNGM132 132.00 | T1 | RNGM132 | RNGM132T1 | 4.3905 | RNGM132 132.00 | T1 | RNGM132 | RNGM132T1 | 4.3905 | 97111
[12 empty] | 97111 | RNGM132 132.00 | T2 | RNGM132 | RNGM132T2 | 4.4765 | RNGM132 132.00 | T2 | RNGM132 | RNGM132T2 | 4.4765 | 97111
[12 empty] | 97124 | RNGT132 132.00 | T1 | RNGT132 | RNGT132T1 | 7.9526 | RNGT132 132.00 | T1 | RNGT132 | RNGT132T1 | 7.9526 | 97124
[12 empty] | 97124 | RNGT132 132.00 | T2 | RNGT132 | RNGT132T2 | 6.7204 | RNGT132 132.00 | T2 | RNGT132 | RNGT132T2 | 6.7204 | 97124
[12 empty] | 97124 | RNGT132 132.00 | T3 | RNGT132 | RNGT132T3 | 9.0824 | RNGT132 132.00 | T3 | RNGT132 | RNGT132T3 | 9.0824 | 97124
[12 empty] | 97134 | SABG132 132.00 | T1 | SABG132 | SABG132T1 | 10.094 | SABG132 132.00 | T1 | SABG132 | SABG132T1 | 10.094 | 97134
[12 empty] | 97134 | SABG132 132.00 | T2 | SABG132 | SABG132T2 | 11.085 | SABG132 132.00 | T2 | SABG132 | SABG132T2 | 11.085 | 97134
[12 empty] | 97134 | SABG132 132.00 | T3 | SABG132 | SABG132T3 | 27.6737 | SABG132 132.00 | T3 | SABG132 | SABG132T3 | 27.6737 | 97134
[12 empty] | 97134 | SABG132 132.00 | T4 | SABG132 | SABG132T4 | 27.331 | SABG132 132.00 | T4 | SABG132 | SABG132T4 | 27.331 | 97134
[12 empty] | 97113 | SDAI132 132.00 | T1 | SDAI132 | SDAI132T1 | 30.0191 | SDAI132 132.00 | T1 | SDAI132 | SDAI132T1 | 30.0191 | 97113
[12 empty] | 97113 | SDAI132 132.00 | T2 | SDAI132 | SDAI132T2 | 29.783 | SDAI132 132.00 | T2 | SDAI132 | SDAI132T2 | 29.783 | 97113
[12 empty] | 97113 | SDAI132 132.00 | T7 | SDAI132 | SDAI132T7 | 0.6275 | SDAI132 132.00 | T7 | SDAI132 | SDAI132T7 | 0.6275 | 97113
[12 empty] | 97113 | SDAI132 132.00 | T8 | SDAI132 | SDAI132T8 | 0.6741 | SDAI132 132.00 | T8 | SDAI132 | SDAI132T8 | 0.6741 | 97113
[12 empty] | 197113 | SDAI132_T9 132.00 | T9 | SDAI132 | SDAI132T9 | 0 | SDAI132_T9 132.00 | T9 | SDAI132 | SDAI132T9 | 0 | 197113
[12 empty] | 97137 | SDNK132 132.00 | T1 | SDNK132 | SDNK132T1 | 2.7731 | SDNK132 132.00 | T1 | SDNK132 | SDNK132T1 | 2.7731 | 97137
[12 empty] | 97137 | SDNK132 132.00 | T2 | SDNK132 | SDNK132T2 | 2.7741 | SDNK132 132.00 | T2 | SDNK132 | SDNK132T2 | 2.7741 | 97137
[12 empty] | 97142 | SELG132 132.00 | T1 | SELG132 | SELG132T1 | 14.6927 | SELG132 132.00 | T1 | SELG132 | SELG132T1 | 14.6927 | 97142
[12 empty] | 97142 | SELG132 132.00 | T2 | SELG132 | SELG132T2 | 14.6927 | SELG132 132.00 | T2 | SELG132 | SELG132T2 | 14.6927 | 97142
[12 empty] | 97146 | SGAD132 132.00 | T1 | SGAD132 | SGAD132T1 | 15.2177 | SGAD132 132.00 | T1 | SGAD132 | SGAD132T1 | 15.2177 | 97146
[12 empty] | 97146 | SGAD132 132.00 | T2 | SGAD132 | SGAD132T2 | 8.7023 | SGAD132 132.00 | T2 | SGAD132 | SGAD132T2 | 8.7023 | 97146
[12 empty] | 97146 | SGAD132 132.00 | T3 | SGAD132 | SGAD132T3 | 11.9062 | SGAD132 132.00 | T3 | SGAD132 | SGAD132T3 | 11.9062 | 97146
[12 empty] | 97146 | SGAD132 132.00 | T4 | SGAD132 | SGAD132T4 | 10.7537 | SGAD132 132.00 | T4 | SGAD132 | SGAD132T4 | 10.7537 | 97146
[12 empty] | 97141 | SGMT132 132.00 | T1 | SGMT132 | SGMT132T1 | 7.9878 | SGMT132 132.00 | T1 | SGMT132 | SGMT132T1 | 7.9878 | 97141
[12 empty] | 97141 | SGMT132 132.00 | T2 | SGMT132 | SGMT132T2 | 9.8466 | SGMT132 132.00 | T2 | SGMT132 | SGMT132T2 | 9.8466 | 97141
[12 empty] | 97126 | SHTE132 132.00 | T1 | SHTE132 | SHTE132T1 | 33.749 | SHTE132 132.00 | T1 | SHTE132 | SHTE132T1 | 33.749 | 97126
[12 empty] | 97126 | SHTE132 132.00 | T2 | SHTE132 | SHTE132T2 | 33.5108 | SHTE132 132.00 | T2 | SHTE132 | SHTE132T2 | 33.5108 | 97126
[12 empty] | 97251 | SIDC275 275.00 | T1 | SIDC275 | SIDC275T1 | 0 | SIDC275 275.00 | T1 | SIDC275 | SIDC275T1 | 0 | 97251
[12 empty] | 97251 | SIDC275 275.00 | T2 | SIDC275 | SIDC275T2 | 0 | SIDC275 275.00 | T2 | SIDC275 | SIDC275T2 | 0 | 97251
[12 empty] | 97190 | SKRG132 132.00 | T1 | SKRG132 | SKRG132T1 | 2.1176 | SKRG132 132.00 | T1 | SKRG132 | SKRG132T1 | 2.1176 | 97190
[12 empty] | 597190 | SKRG132R 132.00 | T2 | SKRG132 | SKRG132T2 | 2.3754 | SKRG132R 132.00 | T2 | SKRG132 | SKRG132T2 | 2.3754 | 597190
[12 empty] | 97143 | SLNG132 132.00 | T1 | SLNG132 | SLNG132T1 | 12.4767 | SLNG132 132.00 | T1 | SLNG132 | SLNG132T1 | 12.4767 | 97143
[12 empty] | 97143 | SLNG132 132.00 | T2 | SLNG132 | SLNG132T2 | 13.5661 | SLNG132 132.00 | T2 | SLNG132 | SLNG132T2 | 13.5661 | 97143
[12 empty] | 97143 | SLNG132 132.00 | T3 | SLNG132 | SLNG132T3 | 29.1514 | SLNG132 132.00 | T3 | SLNG132 | SLNG132T3 | 29.1514 | 97143
[12 empty] | 97143 | SLNG132 132.00 | T4 | SLNG132 | SLNG132T4 | 29.0064 | SLNG132 132.00 | T4 | SLNG132 | SLNG132T4 | 29.0064 | 97143
[12 empty] | 97154 | SMTI132 132.00 | T1 | SMTI132 | SMTI132T1 | 9.2491 | SMTI132 132.00 | T1 | SMTI132 | SMTI132T1 | 9.2491 | 97154
[12 empty] | 97154 | SMTI132 132.00 | T2 | SMTI132 | SMTI132T2 | 9.509 | SMTI132 132.00 | T2 | SMTI132 | SMTI132T2 | 9.509 | 97154
[12 empty] | 97154 | SMTI132 132.00 | T3 | SMTI132 | SMTI132T3 | 6.9233 | SMTI132 132.00 | T3 | SMTI132 | SMTI132T3 | 6.9233 | 97154
[12 empty] | 97154 | SMTI132 132.00 | T4 | SMTI132 | SMTI132T4 | 7.1253 | SMTI132 132.00 | T4 | SMTI132 | SMTI132T4 | 7.1253 | 97154
[12 empty] | 97162 | SNAI132 132.00 | T1 | SNAI132 | SNAI132T1 | 9.6219 | SNAI132 132.00 | T1 | SNAI132 | SNAI132T1 | 9.6219 | 97162
[12 empty] | 97162 | SNAI132 132.00 | T2 | SNAI132 | SNAI132T2 | 9.6229 | SNAI132 132.00 | T2 | SNAI132 | SNAI132T2 | 9.6229 | 97162
[12 empty] | 97162 | SNAI132 132.00 | T3 | SNAI132 | SNAI132T3 | 43.0695 | SNAI132 132.00 | T3 | SNAI132 | SNAI132T3 | 43.0695 | 97162
[12 empty] | 97162 | SNAI132 132.00 | T4 | SNAI132 | SNAI132T4 | 42.6719 | SNAI132 132.00 | T4 | SNAI132 | SNAI132T4 | 42.6719 | 97162
[12 empty] | 96115 | SRBI132 132.00 | T1 | SRBI132 | SRBI132T1 | 6.2078 | SRBI132 132.00 | T1 | SRBI132 | SRBI132T1 | 6.2078 | 96115
[12 empty] | 96115 | SRBI132 132.00 | T2 | SRBI132 | SRBI132T2 | 6.2182 | SRBI132 132.00 | T2 | SRBI132 | SRBI132T2 | 6.2182 | 96115
[12 empty] | 97139 | SRGM132 132.00 | T1 | SRGM132 | SRGM132T1 | 11.8295 | SRGM132 132.00 | T1 | SRGM132 | SRGM132T1 | 11.8295 | 97139
[12 empty] | 97139 | SRGM132 132.00 | T2 | SRGM132 | SRGM132T2 | 9.1435 | SRGM132 132.00 | T2 | SRGM132 | SRGM132T2 | 9.1435 | 97139
[12 empty] | 97125 | SSLG132 132.00 | T3 | SSLG132 | SSLG132T3 | 4.5013 | SSLG132 132.00 | T3 | SSLG132 | SSLG132T3 | 4.5013 | 97125
[12 empty] | 97125 | SSLG132 132.00 | T4 | SSLG132 | SSLG132T4 | 4.5106 | SSLG132 132.00 | T4 | SSLG132 | SSLG132T4 | 4.5106 | 97125
[12 empty] | 97254 | STDC275 275.00 | T1 | STDC275 | STDC275T1 | 2.189 | STDC275 275.00 | T1 | STDC275 | STDC275T1 | 2.189 | 97254
[12 empty] | 97254 | STDC275 275.00 | T2 | STDC275 | STDC275T2 | 2.189 | STDC275 275.00 | T2 | STDC275 | STDC275T2 | 2.189 | 97254
[12 empty] | 97254 | STDC275 275.00 | T3 | STDC275 | STDC275T3 | 2.189 | STDC275 275.00 | T3 | STDC275 | STDC275T3 | 2.189 | 97254
[12 empty] | 97254 | STDC275 275.00 | T4 | STDC275 | STDC275T4 | 2.189 | STDC275 275.00 | T4 | STDC275 | STDC275T4 | 2.189 | 97254
[12 empty] | 97152 | STUL132 132.00 | T1 | STUL132 | STUL132T1 | 5.2914 | STUL132 132.00 | T1 | STUL132 | STUL132T1 | 5.2914 | 97152
[12 empty] | 97152 | STUL132 132.00 | T2 | STUL132 | STUL132T2 | 5.2779 | STUL132 132.00 | T2 | STUL132 | STUL132T2 | 5.2779 | 97152
[12 empty] | 97101 | TAGS132 132.00 | T1 | TAGS132 | TAGS132T1 | 6.2938 | TAGS132 132.00 | T1 | TAGS132 | TAGS132T1 | 6.2938 | 97101
[12 empty] | 97101 | TAGS132 132.00 | T2 | TAGS132 | TAGS132T2 | 12.2655 | TAGS132 132.00 | T2 | TAGS132 | TAGS132T2 | 12.2655 | 97101
[12 empty] | 97135 | TBKR132 132.00 | T1 | TBKR132 | TBKR132T1 | 0.6762 | TBKR132 132.00 | T1 | TBKR132 | TBKR132T1 | 0.6762 | 97135
[12 empty] | 97135 | TBKR132 132.00 | T2 | TBKR132 | TBKR132T2 | 0.6834 | TBKR132 132.00 | T2 | TBKR132 | TBKR132T2 | 0.6834 | 97135
[12 empty] | 97186 | TBRU132 132.00 | T1 | TBRU132 | TBRU132T1 | 23.2293 | TBRU132 132.00 | T1 | TBRU132 | TBRU132T1 | 23.2293 | 97186
[12 empty] | 97186 | TBRU132 132.00 | T2 | TBRU132 | TBRU132T2 | 0 | TBRU132 132.00 | T2 | TBRU132 | TBRU132T2 | 0 | 97186
[12 empty] | 97186 | TBRU132 132.00 | T3 | TBRU132 | TBRU132T3 | 40.3223 | TBRU132 132.00 | T3 | TBRU132 | TBRU132T3 | 40.3223 | 97186
[12 empty] | 97186 | TBRU132 132.00 | T4 | TBRU132 | TBRU132T4 | 39.614 | TBRU132 132.00 | T4 | TBRU132 | TBRU132T4 | 39.614 | 97186
[12 empty] | 97128 | TKAK132 132.00 | T3 | TKAK132 | TKAK132T3 | 11.1461 | TKAK132 132.00 | T3 | TKAK132 | TKAK132T3 | 11.1461 | 97128
[12 empty] | 97128 | TKAK132 132.00 | T4 | TKAK132 | TKAK132T4 | 11.2041 | TKAK132 132.00 | T4 | TKAK132 | TKAK132T4 | 11.2041 | 97128
[12 empty] | 97166 | TKPG132 132.00 | T1 | TKPG132 | TKPG132T1 | 5.6683 | TKPG132 132.00 | T1 | TKPG132 | TKPG132T1 | 5.6683 | 97166
[12 empty] | 97166 | TKPG132 132.00 | T2 | TKPG132 | TKPG132T2 | 5.9603 | TKPG132 132.00 | T2 | TKPG132 | TKPG132T2 | 5.9603 | 97166
[12 empty] | 97166 | TKPG132 132.00 | T3 | TKPG132 | TKPG132T3 | 15.0562 | TKPG132 132.00 | T3 | TKPG132 | TKPG132T3 | 15.0562 | 97166
[12 empty] | 97166 | TKPG132 132.00 | T4 | TKPG132 | TKPG132T4 | 15.0147 | TKPG132 132.00 | T4 | TKPG132 | TKPG132T4 | 15.0147 | 97166
[12 empty] | 97180 | TLBH132 132.00 | T1 | TLBH132 | TLBH132T1 | 12.6745 | TLBH132 132.00 | T1 | TLBH132 | TLBH132T1 | 12.6745 | 97180
[12 empty] | 97180 | TLBH132 132.00 | T2 | TLBH132 | TLBH132T2 | 12.2738 | TLBH132 132.00 | T2 | TLBH132 | TLBH132T2 | 12.2738 | 97180
[12 empty] | 97184 | TLST132 132.00 | T1 | TLST132 | TLST132T1 | 8.429 | TLST132 132.00 | T1 | TLST132 | TLST132T1 | 8.429 | 97184
[12 empty] | 97184 | TLST132 132.00 | T2 | TLST132 | TLST132T2 | 8.4507 | TLST132 132.00 | T2 | TLST132 | TLST132T2 | 8.4507 | 97184
[12 empty] | 97184 | TLST132 132.00 | T3 | TLST132 | TLST132T3 | 8.8701 | TLST132 132.00 | T3 | TLST132 | TLST132T3 | 8.8701 | 97184
[12 empty] | 97184 | TLST132 132.00 | T4 | TLST132 | TLST132T4 | 8.5304 | TLST132 132.00 | T4 | TLST132 | TLST132T4 | 8.5304 | 97184
[12 empty] | 97184 | TLST132 132.00 | T5 | TLST132 | TLST132T5 | 24.6884 | TLST132 132.00 | T5 | TLST132 | TLST132T5 | 24.6884 | 97184
[12 empty] | 97184 | TLST132 132.00 | T6 | TLST132 | TLST132T6 | 24.6832 | TLST132 132.00 | T6 | TLST132 | TLST132T6 | 24.6832 | 97184
[12 empty] | 97192 | TMPI132 132.00 | T1 | TMPI132 | TMPI132T1 | 29.0913 | TMPI132 132.00 | T1 | TMPI132 | TMPI132T1 | 29.0913 | 97192
[12 empty] | 97192 | TMPI132 132.00 | T2 | TMPI132 | TMPI132T2 | 27.9139 | TMPI132 132.00 | T2 | TMPI132 | TMPI132T2 | 27.9139 | 97192
[12 empty] | 97121 | TPCH132 132.00 | T1 | TPCH132 | TPCH132T1 | 11.4329 | TPCH132 132.00 | T1 | TPCH132 | TPCH132T1 | 11.4329 | 97121
[12 empty] | 97121 | TPCH132 132.00 | T2 | TPCH132 | TPCH132T2 | 4.8668 | TPCH132 132.00 | T2 | TPCH132 | TPCH132T2 | 4.8668 | 97121
[12 empty] | 97127 | TPOI132 132.00 | T1 | TPOI132 | TPOI132T1 | 11.9093 | TPOI132 132.00 | T1 | TPOI132 | TPOI132T1 | 11.9093 | 97127
[12 empty] | 97127 | TPOI132 132.00 | T2 | TPOI132 | TPOI132T2 | 11.9165 | TPOI132 132.00 | T2 | TPOI132 | TPOI132T2 | 11.9165 | 97127
[12 empty] | 97130 | TRMN132 132.00 | T1 | TRMN132 | TRMN132T1 | 2.4345 | TRMN132 132.00 | T1 | TRMN132 | TRMN132T1 | 2.4345 | 97130
[12 empty] | 97130 | TRMN132 132.00 | T2 | TRMN132 | TRMN132T2 | 2.4096 | TRMN132 132.00 | T2 | TRMN132 | TRMN132T2 | 2.4096 | 97130
[12 empty] | 97130 | TRMN132 132.00 | T3 | TRMN132 | TRMN132T3 | 7.3655 | TRMN132 132.00 | T3 | TRMN132 | TRMN132T3 | 7.3655 | 97130
[12 empty] | 97130 | TRMN132 132.00 | T4 | TRMN132 | TRMN132T4 | 6.8788 | TRMN132 132.00 | T4 | TRMN132 | TRMN132T4 | 6.8788 | 97130
[12 empty] | 97144 | TTKJ132 132.00 | T1 | TTKJ132 | TTKJ132T1 | 0 | TTKJ132 132.00 | T1 | TTKJ132 | TTKJ132T1 | 0 | 97144
[12 empty] | 97144 | TTKJ132 132.00 | T2 | TTKJ132 | TTKJ132T2 | 0 | TTKJ132 132.00 | T2 | TTKJ132 | TTKJ132T2 | 0 | 97144
[12 empty] | 97195 | TUNI132 132.00 | T1 | TUNI132 | TUNI132T1 | 11.5821 | TUNI132 132.00 | T1 | TUNI132 | TUNI132T1 | 11.5821 | 97195
[12 empty] | 97195 | TUNI132 132.00 | T2 | TUNI132 | TUNI132T2 | 18.0301 | TUNI132 132.00 | T2 | TUNI132 | TUNI132T2 | 18.0301 | 97195
[12 empty] | 97188 | UTRM132 132.00 | T1 | UTRM132 | UTRM132T1 | 9.2791 | UTRM132 132.00 | T1 | UTRM132 | UTRM132T1 | 9.2791 | 97188
[12 empty] | 97188 | UTRM132 132.00 | T2 | UTRM132 | UTRM132T2 | 9.3102 | UTRM132 132.00 | T2 | UTRM132 | UTRM132T2 | 9.3102 | 97188
[12 empty] | 97188 | UTRM132 132.00 | T3 | UTRM132 | UTRM132T3 | 30.5555 | UTRM132 132.00 | T3 | UTRM132 | UTRM132T3 | 30.5555 | 97188
[12 empty] | 97188 | UTRM132 132.00 | T4 | UTRM132 | UTRM132T4 | 29.6836 | UTRM132 132.00 | T4 | UTRM132 | UTRM132T4 | 29.6836 | 97188
[12 empty] | 97107 | YGPG132 132.00 | T1 | YGPG132 | YGPG132T1 | 11.4443 | YGPG132 132.00 | T1 | YGPG132 | YGPG132T1 | 11.4443 | 97107
[12 empty] | 97107 | YGPG132 132.00 | T2 | YGPG132 | YGPG132T2 | 9.8683 | YGPG132 132.00 | T2 | YGPG132 | YGPG132T2 | 9.8683 | 97107
[12 empty] | 97107 | YGPG132 132.00 | T3 | YGPG132 | YGPG132T3 | 0 | YGPG132 132.00 | T3 | YGPG132 | YGPG132T3 | 0 | 97107
[12 empty] | 97107 | YGPG132 132.00 | T4 | YGPG132 | YGPG132T4 | 11.0736 | YGPG132 132.00 | T4 | YGPG132 | YGPG132T4 | 11.0736 | 97107
[12 empty] | 74104 | ATNI132 132.00 | T1 | ATNI132 | ATNI132T1 | 3.5973 | ATNI132 132.00 | T1 | ATNI132 | ATNI132T1 | 3.5973 | 74104
[12 empty] | 74104 | ATNI132 132.00 | T2 | ATNI132 | ATNI132T2 | 4.1006 | ATNI132 132.00 | T2 | ATNI132 | ATNI132T2 | 4.1006 | 74104
[12 empty] | 74128 | BIMK132 132.00 | T1 | BIMK132 | BIMK132T1 | 10.0526 | BIMK132 132.00 | T1 | BIMK132 | BIMK132T1 | 10.0526 | 74128
[12 empty] | 74128 | BIMK132 132.00 | T2 | BIMK132 | BIMK132T2 | 11.2828 | BIMK132 132.00 | T2 | BIMK132 | BIMK132T2 | 11.2828 | 74128
[12 empty] | 74128 | BIMK132 132.00 | T3 | BIMK132 | BIMK132T3 | 37.4146 | BIMK132 132.00 | T3 | BIMK132 | BIMK132T3 | 37.4146 | 74128
[12 empty] | 74128 | BIMK132 132.00 | T4 | BIMK132 | BIMK132T4 | 37.6424 | BIMK132 132.00 | T4 | BIMK132 | BIMK132T4 | 37.6424 | 74128
[12 empty] | 74112 | BMSH132 132.00 | T1 | BMSH132 | BMSH132T1 | 11.959 | BMSH132 132.00 | T1 | BMSH132 | BMSH132T1 | 11.959 | 74112
[12 empty] | 74112 | BMSH132 132.00 | T2 | BMSH132 | BMSH132T2 | 11.9041 | BMSH132 132.00 | T2 | BMSH132 | BMSH132T2 | 11.9041 | 74112
[12 empty] | 74120 | BNTA132 132.00 | T1 | BNTA132 | BNTA132T1 | 2.7813 | BNTA132 132.00 | T1 | BNTA132 | BNTA132T1 | 2.7813 | 74120
[12 empty] | 74120 | BNTA132 132.00 | T2 | BNTA132 | BNTA132T2 | 2.7896 | BNTA132 132.00 | T2 | BNTA132 | BNTA132T2 | 2.7896 | 74120
[12 empty] | 74118 | BNTG132 132.00 | T1 | BNTG132 | BNTG132T1 | 8.081 | BNTG132 132.00 | T1 | BNTG132 | BNTG132T1 | 8.081 | 74118
[12 empty] | 74118 | BNTG132 132.00 | T2 | BNTG132 | BNTG132T2 | 11.3387 | BNTG132 132.00 | T2 | BNTG132 | BNTG132T2 | 11.3387 | 74118
[12 empty] | 74101 | BTRT132 132.00 | T1 | BTRT132 | BTRT132T1 | 0.5457 | BTRT132 132.00 | T1 | BTRT132 | BTRT132T1 | 0.5457 | 74101
[12 empty] | 74101 | BTRT132 132.00 | T2 | BTRT132 | BTRT132T2 | 0.5478 | BTRT132 132.00 | T2 | BTRT132 | BTRT132T2 | 0.5478 | 74101
[12 empty] | 74150 | CUFG132 132.00 | 99 | CUFG132 | CUFG13299 | 0 | CUFG132 132.00 | 99 | CUFG132 | CUFG13299 | 0 | 74150
[12 empty] | 74137 | GBID132 132.00 | T1 | GBID132 | GBID132T1 | 22.3958 | GBID132 132.00 | T1 | GBID132 | GBID132T1 | 22.3958 | 74137
[12 empty] | 74137 | GBID132 132.00 | T2 | GBID132 | GBID132T2 | 0 | GBID132 132.00 | T2 | GBID132 | GBID132T2 | 0 | 74137
[12 empty] | 74138 | GBNG132 132.00 | T1 | GBNG132 | GBNG132T1 | 2.7917 | GBNG132 132.00 | T1 | GBNG132 | GBNG132T1 | 2.7917 | 74138
[12 empty] | 74138 | GBNG132 132.00 | T2 | GBNG132 | GBNG132T2 | 7.7517 | GBNG132 132.00 | T2 | GBNG132 | GBNG132T2 | 7.7517 | 74138
[12 empty] | 74138 | GBNG132 132.00 | T3 | GBNG132 | GBNG132T3 | 12.6144 | GBNG132 132.00 | T3 | GBNG132 | GBNG132T3 | 12.6144 | 74138
[12 empty] | 74138 | GBNG132 132.00 | T4 | GBNG132 | GBNG132T4 | 12.4167 | GBNG132 132.00 | T4 | GBNG132 | GBNG132T4 | 12.4167 | 74138
[12 empty] | 74125 | GTNG132 132.00 | T1 | GTNG132 | GTNG132T1 | 1.0024 | GTNG132 132.00 | T1 | GTNG132 | GTNG132T1 | 1.0024 | 74125
[12 empty] | 74125 | GTNG132 132.00 | T2 | GTNG132 | GTNG132T2 | 5.9552 | GTNG132 132.00 | T2 | GTNG132 | GTNG132T2 | 5.9552 | 74125
[12 empty] | 74135 | JBRS132 132.00 | T1 | JBRS132 | JBRS132T1 | 9.0151 | JBRS132 132.00 | T1 | JBRS132 | JBRS132T1 | 9.0151 | 74135
[12 empty] | 74135 | JBRS132 132.00 | T2 | JBRS132 | JBRS132T2 | 7.8035 | JBRS132 132.00 | T2 | JBRS132 | JBRS132T2 | 7.8035 | 74135
[12 empty] | 74135 | JBRS132 132.00 | T3 | JBRS132 | JBRS132T3 | 4.1958 | JBRS132 132.00 | T3 | JBRS132 | JBRS132T3 | 4.1958 | 74135
[12 empty] | 74135 | JBRS132 132.00 | T4 | JBRS132 | JBRS132T4 | 4.1772 | JBRS132 132.00 | T4 | JBRS132 | JBRS132T4 | 4.1772 | 74135
[12 empty] | 74123 | JNKA132 132.00 | T1 | JNKA132 | JNKA132T1 | 12.5948 | JNKA132 132.00 | T1 | JNKA132 | JNKA132T1 | 12.5948 | 74123
[12 empty] | 74123 | JNKA132 132.00 | T2 | JNKA132 | JNKA132T2 | 12.6745 | JNKA132 132.00 | T2 | JNKA132 | JNKA132T2 | 12.6745 | 74123
[12 empty] | 74123 | JNKA132 132.00 | T7 | JNKA132 | JNKA132T7 | 5.542 | JNKA132 132.00 | T7 | JNKA132 | JNKA132T7 | 5.542 | 74123
[12 empty] | 74122 | JTUT132 132.00 | T1 | JTUT132 | JTUT132T1 | 19.1629 | JTUT132 132.00 | T1 | JTUT132 | JTUT132T1 | 19.1629 | 74122
[12 empty] | 74122 | JTUT132 132.00 | T2 | JTUT132 | JTUT132T2 | 18.9921 | JTUT132 132.00 | T2 | JTUT132 | JTUT132T2 | 18.9921 | 74122
[12 empty] | 74110 | KAWA132 132.00 | T1 | KAWA132 | KAWA132T1 | 9.2915 | KAWA132 132.00 | T1 | KAWA132 | KAWA132T1 | 9.2915 | 74110
[12 empty] | 74110 | KAWA132 132.00 | T2 | KAWA132 | KAWA132T2 | 9.2025 | KAWA132 132.00 | T2 | KAWA132 | KAWA132T2 | 9.2025 | 74110
[12 empty] | 74121 | KLIP132 132.00 | T1 | KLIP132 | KLIP132T1 | 11.407 | KLIP132 132.00 | T1 | KLIP132 | KLIP132T1 | 11.407 | 74121
[12 empty] | 74121 | KLIP132 132.00 | T2 | KLIP132 | KLIP132T2 | 5.9976 | KLIP132 132.00 | T2 | KLIP132 | KLIP132T2 | 5.9976 | 74121
[12 empty] | 74121 | KLIP132 132.00 | T3 | KLIP132 | KLIP132T3 | 12.9841 | KLIP132 132.00 | T3 | KLIP132 | KLIP132T3 | 12.9841 | 74121
[12 empty] | 74121 | KLIP132 132.00 | T4 | KLIP132 | KLIP132T4 | 12.4798 | KLIP132 132.00 | T4 | KLIP132 | KLIP132T4 | 12.4798 | 74121
[12 empty] | 74116 | KRAK132 132.00 | T1 | KRAK132 | KRAK132T1 | 2.0089 | KRAK132 132.00 | T1 | KRAK132 | KRAK132T1 | 2.0089 | 74116
[12 empty] | 74116 | KRAK132 132.00 | T2 | KRAK132 | KRAK132T2 | 1.6993 | KRAK132 132.00 | T2 | KRAK132 | KRAK132T2 | 1.6993 | 74116
[12 empty] | 74116 | KRAK132 132.00 | T3 | KRAK132 | KRAK132T3 | 3.0061 | KRAK132 132.00 | T3 | KRAK132 | KRAK132T3 | 3.0061 | 74116
[12 empty] | 74116 | KRAK132 132.00 | T4 | KRAK132 | KRAK132T4 | 2.9978 | KRAK132 132.00 | T4 | KRAK132 | KRAK132T4 | 2.9978 | 74116
[12 empty] | 74145 | KRYG132 132.00 | T1 | KRYG132 | KRYG132T1 | 31.6769 | KRYG132 132.00 | T1 | KRYG132 | KRYG132T1 | 31.6769 | 74145
[12 empty] | 74145 | KRYG132 132.00 | T2 | KRYG132 | KRYG132T2 | 0 | KRYG132 132.00 | T2 | KRYG132 | KRYG132T2 | 0 | 74145
[12 empty] | 74108 | KTAN132 132.00 | T1 | KTAN132 | KTAN132T1 | 15.1411 | KTAN132 132.00 | T1 | KTAN132 | KTAN132T1 | 15.1411 | 74108
[12 empty] | 74108 | KTAN132 132.00 | T2 | KTAN132 | KTAN132T2 | 15.7603 | KTAN132 132.00 | T2 | KTAN132 | KTAN132T2 | 15.7603 | 74108
[12 empty] | 74108 | KTAN132 132.00 | T3 | KTAN132 | KTAN132T3 | 14.8553 | KTAN132 132.00 | T3 | KTAN132 | KTAN132T3 | 14.8553 | 74108
[12 empty] | 74108 | KTAN132 132.00 | T4 | KTAN132 | KTAN132T4 | 26.0345 | KTAN132 132.00 | T4 | KTAN132 | KTAN132T4 | 26.0345 | 74108
[12 empty] | 74108 | KTAN132 132.00 | T5 | KTAN132 | KTAN132T5 | 26.1349 | KTAN132 132.00 | T5 | KTAN132 | KTAN132T5 | 26.1349 | 74108
[12 empty] | 74141 | KTCL132 132.00 | T1 | KTCL132 | KTCL132T1 | 8.4994 | KTCL132 132.00 | T1 | KTCL132 | KTCL132T1 | 8.4994 | 74141
[12 empty] | 74141 | KTCL132 132.00 | T2 | KTCL132 | KTCL132T2 | 8.2198 | KTCL132 132.00 | T2 | KTCL132 | KTCL132T2 | 8.2198 | 74141
[12 empty] | 74132 | KTRI132 132.00 | T1 | KTRI132 | KTRI132T1 | 0 | KTRI132 132.00 | T1 | KTRI132 | KTRI132T1 | 0 | 74132
[12 empty] | 74143 | MECC132 132.00 | T1 | MECC132 | MECC132T1 | 6.8643 | MECC132 132.00 | T1 | MECC132 | MECC132T1 | 6.8643 | 74143
[12 empty] | 74143 | MECC132 132.00 | T2 | MECC132 | MECC132T2 | 6.9254 | MECC132 132.00 | T2 | MECC132 | MECC132T2 | 6.9254 | 74143
[12 empty] | 74143 | MECC132 132.00 | T3 | MECC132 | MECC132T3 | 0.9433 | MECC132 132.00 | T3 | MECC132 | MECC132T3 | 0.9433 | 74143
[12 empty] | 74143 | MECC132 132.00 | T4 | MECC132 | MECC132T4 | 0.9216 | MECC132 132.00 | T4 | MECC132 | MECC132T4 | 0.9216 | 74143
[12 empty] | 74129 | MRAN132 132.00 | T1 | MRAN132 | MRAN132T1 | 4.493 | MRAN132 132.00 | T1 | MRAN132 | MRAN132T1 | 4.493 | 74129
[12 empty] | 74129 | MRAN132 132.00 | T2 | MRAN132 | MRAN132T2 | 4.5531 | MRAN132 132.00 | T2 | MRAN132 | MRAN132T2 | 4.5531 | 74129
[12 empty] | 74117 | MTKB132 132.00 | T1 | MTKB132 | MTKB132T1 | 0 | MTKB132 132.00 | T1 | MTKB132 | MTKB132T1 | 0 | 74117
[12 empty] | 74117 | MTKB132 132.00 | T2 | MTKB132 | MTKB132T2 | 22.578 | MTKB132 132.00 | T2 | MTKB132 | MTKB132T2 | 22.578 | 74117
[12 empty] | 74109 | PKAN132 132.00 | T1 | PKAN132 | PKAN132T1 | 4.6742 | PKAN132 132.00 | T1 | PKAN132 | PKAN132T1 | 4.6742 | 74109
[12 empty] | 74109 | PKAN132 132.00 | T2 | PKAN132 | PKAN132T2 | 4.6815 | PKAN132 132.00 | T2 | PKAN132 | PKAN132T2 | 4.6815 | 74109
[12 empty] | 74109 | PKAN132 132.00 | T3 | PKAN132 | PKAN132T3 | 6.3994 | PKAN132 132.00 | T3 | PKAN132 | PKAN132T3 | 6.3994 | 74109
[12 empty] | 74115 | PKNI132 132.00 | T1 | PKNI132 | PKNI132T1 | 6.2824 | PKNI132 132.00 | T1 | PKNI132 | PKNI132T1 | 6.2824 | 74115
[12 empty] | 74115 | PKNI132 132.00 | T2 | PKNI132 | PKNI132T2 | 6.3124 | PKNI132 132.00 | T2 | PKNI132 | PKNI132T2 | 6.3124 | 74115
[12 empty] | 174920 | PNLS132 132.00 | T1 | PNLS132 | PNLS132T1 | 0 | PNLS132 132.00 | T1 | PNLS132 | PNLS132T1 | 0 | 174920
[12 empty] | 74151 | RBDR132 132.00 | T1 | RBDR132 | RBDR132T1 | 11.7011 | RBDR132 132.00 | T1 | RBDR132 | RBDR132T1 | 11.7011 | 74151
[12 empty] | 74151 | RBDR132 132.00 | T2 | RBDR132 | RBDR132T2 | 11.0332 | RBDR132 132.00 | T2 | RBDR132 | RBDR132T2 | 11.0332 | 74151
[12 empty] | 74151 | RBDR132 132.00 | T3 | RBDR132 | RBDR132T3 | 0 | RBDR132 132.00 | T3 | RBDR132 | RBDR132T3 | 0 | 74151
[12 empty] | 74151 | RBDR132 132.00 | T4 | RBDR132 | RBDR132T4 | 0 | RBDR132 132.00 | T4 | RBDR132 | RBDR132T4 | 0 | 74151
[12 empty] | 74107 | SMBU132 132.00 | T1 | SMBU132 | SMBU132T1 | 10.6066 | SMBU132 132.00 | T1 | SMBU132 | SMBU132T1 | 10.6066 | 74107
[12 empty] | 74107 | SMBU132 132.00 | T2 | SMBU132 | SMBU132T2 | 6.0825 | SMBU132 132.00 | T2 | SMBU132 | SMBU132T2 | 6.0825 | 74107
[12 empty] | 74127 | SONG132 132.00 | T1 | SONG132 | SONG132T1 | 14.467 | SONG132 132.00 | T1 | SONG132 | SONG132T1 | 14.467 | 74127
[12 empty] | 74127 | SONG132 132.00 | T2 | SONG132 | SONG132T2 | 7.612 | SONG132 132.00 | T2 | SONG132 | SONG132T2 | 7.612 | 74127
[12 empty] | 74157 | TAGP132 132.00 | T7 | TAGP132 | TAGP132T7 | 3.5787 | TAGP132 132.00 | T7 | TAGP132 | TAGP132T7 | 3.5787 | 74157
[12 empty] | 74106 | TGLN132 132.00 | T1 | TGLN132 | TGLN132T1 | 5.9562 | TGLN132 132.00 | T1 | TGLN132 | TGLN132T1 | 5.9562 | 74106
[12 empty] | 74106 | TGLN132 132.00 | T2 | TGLN132 | TGLN132T2 | 5.2148 | TGLN132 132.00 | T2 | TGLN132 | TGLN132T2 | 5.2148 | 74106
[12 empty] | 74106 | TGLN132 132.00 | T3 | TGLN132 | TGLN132T3 | 11.2642 | TGLN132 132.00 | T3 | TGLN132 | TGLN132T3 | 11.2642 | 74106
[12 empty] | 74133 | TGMK132 132.00 | T1 | TGMK132 | TGMK132T1 | 13.7514 | TGMK132 132.00 | T1 | TGMK132 | TGMK132T1 | 13.7514 | 74133
[12 empty] | 74133 | TGMK132 132.00 | T2 | TGMK132 | TGMK132T2 | 13.7411 | TGMK132 132.00 | T2 | TGMK132 | TGMK132T2 | 13.7411 | 74133
[12 empty] | 74111 | TJBU132 132.00 | T1 | TJBU132 | TJBU132T1 | 2.1818 | TJBU132 132.00 | T1 | TJBU132 | TJBU132T1 | 2.1818 | 74111
[12 empty] | 74111 | TJBU132 132.00 | T2 | TJBU132 | TJBU132T2 | 2.2211 | TJBU132 132.00 | T2 | TJBU132 | TJBU132T2 | 2.2211 | 74111
[12 empty] | 74144 | TMID132 132.00 | T1 | TMID132 | TMID132T1 | 9.0399 | TMID132 132.00 | T1 | TMID132 | TMID132T1 | 9.0399 | 74144
[12 empty] | 74144 | TMID132 132.00 | T2 | TMID132 | TMID132T2 | 9.1155 | TMID132 132.00 | T2 | TMID132 | TMID132T2 | 9.1155 | 74144
[12 empty] | 74144 | TMID132 132.00 | T3 | TMID132 | TMID132T3 | 0 | TMID132 132.00 | T3 | TMID132 | TMID132T3 | 0 | 74144
[12 empty] | 74144 | TMID132 132.00 | T4 | TMID132 | TMID132T4 | 0 | TMID132 132.00 | T4 | TMID132 | TMID132T4 | 0 | 74144
[12 empty] | 74156 | UIAM132 132.00 | T1 | UIAM132 | UIAM132T1 | 8.196 | UIAM132 132.00 | T1 | UIAM132 | UIAM132T1 | 8.196 | 74156
[12 empty] | 74156 | UIAM132 132.00 | T2 | UIAM132 | UIAM132T2 | 8.197 | UIAM132 132.00 | T2 | UIAM132 | UIAM132T2 | 8.197 | 74156
[12 empty] | 75138 | BRKT132 132.00 | T1 | BRKT132 | BRKT132T1 | 9.1207 | BRKT132 132.00 | T1 | BRKT132 | BRKT132T1 | 9.1207 | 75138
[12 empty] | 75138 | BRKT132 132.00 | T2 | BRKT132 | BRKT132T2 | 9.0182 | BRKT132 132.00 | T2 | BRKT132 | BRKT132T2 | 9.0182 | 75138
[12 empty] | 75138 | BRKT132 132.00 | T3 | BRKT132 | BRKT132T3 | 14.7041 | BRKT132 132.00 | T3 | BRKT132 | BRKT132T3 | 14.7041 | 75138
[12 empty] | 75109 | CHRG132 132.00 | T1 | CHRG132 | CHRG132T1 | 17.8064 | CHRG132 132.00 | T1 | CHRG132 | CHRG132T1 | 17.8064 | 75109
[12 empty] | 75109 | CHRG132 132.00 | T2 | CHRG132 | CHRG132T2 | 14.3209 | CHRG132 132.00 | T2 | CHRG132 | CHRG132T2 | 14.3209 | 75109
[12 empty] | 75109 | CHRG132 132.00 | T3 | CHRG132 | CHRG132T3 | 25.6648 | CHRG132 132.00 | T3 | CHRG132 | CHRG132T3 | 25.6648 | 75109
[12 empty] | 75109 | CHRG132 132.00 | T4 | CHRG132 | CHRG132T4 | 26.2426 | CHRG132 132.00 | T4 | CHRG132 | CHRG132T4 | 26.2426 | 75109
[12 empty] | 75144 | CKAI132 132.00 | T1 | CKAI132 | CKAI132T1 | 12.7325 | CKAI132 132.00 | T1 | CKAI132 | CKAI132T1 | 12.7325 | 75144
[12 empty] | 75144 | CKAI132 132.00 | T2 | CKAI132 | CKAI132T2 | 12.7594 | CKAI132 132.00 | T2 | CKAI132 | CKAI132T2 | 12.7594 | 75144
[12 empty] | 75150 | CUFK132 132.00 | 99 | CUFK132 | CUFK13299 | 0 | CUFK132 132.00 | 99 | CUFK132 | CUFK13299 | 0 | 75150
[12 empty] | 75118 | DGID132 132.00 | T1 | DGID132 | DGID132T1 | 0 | DGID132 132.00 | T1 | DGID132 | DGID132T1 | 0 | 75118
[12 empty] | 75118 | DGID132 132.00 | T2 | DGID132 | DGID132T2 | 25.8719 | DGID132 132.00 | T2 | DGID132 | DGID132T2 | 25.8719 | 75118
[12 empty] | 75103 | DGUN132 132.00 | T1 | DGUN132 | DGUN132T1 | 5.2179 | DGUN132 132.00 | T1 | DGUN132 | DGUN132T1 | 5.2179 | 75103
[12 empty] | 75103 | DGUN132 132.00 | T2 | DGUN132 | DGUN132T2 | 5.1723 | DGUN132 132.00 | T2 | DGUN132 | DGUN132T2 | 5.1723 | 75103
[12 empty] | 75116 | GBDK132 132.00 | T1 | GBDK132 | GBDK132T1 | 10.6625 | GBDK132 132.00 | T1 | GBDK132 | GBDK132T1 | 10.6625 | 75116
[12 empty] | 75116 | GBDK132 132.00 | T2 | GBDK132 | GBDK132T2 | 10.6832 | GBDK132 132.00 | T2 | GBDK132 | GBDK132T2 | 10.6832 | 75116
[12 empty] | 75116 | GBDK132 132.00 | T3 | GBDK132 | GBDK132T3 | 19.3752 | GBDK132 132.00 | T3 | GBDK132 | GBDK132T3 | 19.3752 | 75116
[12 empty] | 75116 | GBDK132 132.00 | T4 | GBDK132 | GBDK132T4 | 19.4291 | GBDK132 132.00 | T4 | GBDK132 | GBDK132T4 | 19.4291 | 75116
[12 empty] | 75299 | HTRG275 275.00 | T1 | HTRG275 | HTRG275T1 | 0 | HTRG275 275.00 | T1 | HTRG275 | HTRG275T1 | 0 | 75299
[12 empty] | 75299 | HTRG275 275.00 | T2 | HTRG275 | HTRG275T2 | 0 | HTRG275 275.00 | T2 | HTRG275 | HTRG275T2 | 0 | 75299
[12 empty] | 75926 | HTRG_U3 11.000 | X1 | HTRG_U3 | HTRG_U3X1 | 0 | HTRG_U3 11.000 | X1 | HTRG_U3 | HTRG_U3X1 | 0 | 75926
[12 empty] | 75927 | HTRG_U4 11.000 | X1 | HTRG_U4 | HTRG_U4X1 | 0 | HTRG_U4 11.000 | X1 | HTRG_U4 | HTRG_U4X1 | 0 | 75927
[12 empty] | 75140 | KBRG132 132.00 | T1 | KBRG132 | KBRG132T1 | 10.8862 | KBRG132 132.00 | T1 | KBRG132 | KBRG132T1 | 10.8862 | 75140
[12 empty] | 75140 | KBRG132 132.00 | T2 | KBRG132 | KBRG132T2 | 10.4865 | KBRG132 132.00 | T2 | KBRG132 | KBRG132T2 | 10.4865 | 75140
[12 empty] | 75140 | KBRG132 132.00 | T3 | KBRG132 | KBRG132T3 | 5.0563 | KBRG132 132.00 | T3 | KBRG132 | KBRG132T3 | 5.0563 | 75140
[12 empty] | 75140 | KBRG132 132.00 | T4 | KBRG132 | KBRG132T4 | 5.133 | KBRG132 132.00 | T4 | KBRG132 | KBRG132T4 | 5.133 | 75140
[12 empty] | 75105 | KMAN132 132.00 | T1 | KMAN132 | KMAN132T1 | 9.656 | KMAN132 132.00 | T1 | KMAN132 | KMAN132T1 | 9.656 | 75105
[12 empty] | 75105 | KMAN132 132.00 | T2 | KMAN132 | KMAN132T2 | 9.685 | KMAN132 132.00 | T2 | KMAN132 | KMAN132T2 | 9.685 | 75105
[12 empty] | 75105 | KMAN132 132.00 | T3 | KMAN132 | KMAN132T3 | 2.858 | KMAN132 132.00 | T3 | KMAN132 | KMAN132T3 | 2.858 | 75105
[12 empty] | 75105 | KMAN132 132.00 | T4 | KMAN132 | KMAN132T4 | 2.8777 | KMAN132 132.00 | T4 | KMAN132 | KMAN132T4 | 2.8777 | 75105
[12 empty] | 75102 | KNYR132 132.00 | T1 | KNYR132 | KNYR132T1 | 0 | KNYR132 132.00 | T1 | KNYR132 | KNYR132T1 | 0 | 75102
[12 empty] | 75102 | KNYR132 132.00 | T2 | KNYR132 | KNYR132T2 | 0 | KNYR132 132.00 | T2 | KNYR132 | KNYR132T2 | 0 | 75102
[12 empty] | 75115 | KTGU132 132.00 | T1 | KTGU132 | KTGU132T1 | 13.361 | KTGU132 132.00 | T1 | KTGU132 | KTGU132T1 | 13.361 | 75115
[12 empty] | 75115 | KTGU132 132.00 | T2 | KTGU132 | KTGU132T2 | 11.4909 | KTGU132 132.00 | T2 | KTGU132 | KTGU132T2 | 11.4909 | 75115
[12 empty] | 75115 | KTGU132 132.00 | T3 | KTGU132 | KTGU132T3 | 11.521 | KTGU132 132.00 | T3 | KTGU132 | KTGU132T3 | 11.521 | 75115
[12 empty] | 75115 | KTGU132 132.00 | T4 | KTGU132 | KTGU132T4 | 11.5365 | KTGU132 132.00 | T4 | KTGU132 | KTGU132T4 | 11.5365 | 75115
[12 empty] | 75124 | KTIH132 132.00 | T1 | KTIH132 | KTIH132T1 | 5.9676 | KTIH132 132.00 | T1 | KTIH132 | KTIH132T1 | 5.9676 | 75124
[12 empty] | 75124 | KTIH132 132.00 | T2 | KTIH132 | KTIH132T2 | 5.9614 | KTIH132 132.00 | T2 | KTIH132 | KTIH132T2 | 5.9614 | 75124
[12 empty] | 74261 | MCKP275 275.00 | T1 | MCKP275 | MCKP275T1 | 0.5009 | MCKP275 275.00 | T1 | MCKP275 | MCKP275T1 | 0.5009 | 74261
[12 empty] | 74261 | MCKP275 275.00 | T2 | MCKP275 | MCKP275T2 | 0.5009 | MCKP275 275.00 | T2 | MCKP275 | MCKP275T2 | 0.5009 | 74261
[12 empty] | 75910 | MCLS_LSS1 0.6000 | X1 | MCLS_LS | MCLS_LSX1 | 0 | MCLS_LSS1 0.6000 | X1 | MCLS_LS | MCLS_LSX1 | 0 | 75910
[12 empty] | 75104 | PAKA132 132.00 | NA | PAKA132 | PAKA132NA | 0 | PAKA132 132.00 | NA | PAKA132 | PAKA132NA | 0 | 75104
[12 empty] | 75104 | PAKA132 132.00 | NB | PAKA132 | PAKA132NB | 0 | PAKA132 132.00 | NB | PAKA132 | PAKA132NB | 0 | 75104
[12 empty] | 75104 | PAKA132 132.00 | T1 | PAKA132 | PAKA132T1 | 6.6199 | PAKA132 132.00 | T1 | PAKA132 | PAKA132T1 | 6.6199 | 75104
[12 empty] | 75104 | PAKA132 132.00 | T2 | PAKA132 | PAKA132T2 | 6.5992 | PAKA132 132.00 | T2 | PAKA132 | PAKA132T2 | 6.5992 | 75104
[12 empty] | 75104 | PAKA132 132.00 | T5 | PAKA132 | PAKA132T5 | 2.4407 | PAKA132 132.00 | T5 | PAKA132 | PAKA132T5 | 2.4407 | 75104
[12 empty] | 75104 | PAKA132 132.00 | T6 | PAKA132 | PAKA132T6 | 2.4065 | PAKA132 132.00 | T6 | PAKA132 | PAKA132T6 | 2.4065 | 75104
[12 empty] | 75111 | RPTS132 132.00 | T1 | RPTS132 | RPTS132T1 | 6.4108 | RPTS132 132.00 | T1 | RPTS132 | RPTS132T1 | 6.4108 | 75111
[12 empty] | 75111 | RPTS132 132.00 | T2 | RPTS132 | RPTS132T2 | 6.4046 | RPTS132 132.00 | T2 | RPTS132 | RPTS132T2 | 6.4046 | 75111
[12 empty] | 75120 | STNG132 132.00 | T1 | STNG132 | STNG132T1 | 6.4594 | STNG132 132.00 | T1 | STNG132 | STNG132T1 | 6.4594 | 75120
[12 empty] | 75120 | STNG132 132.00 | T2 | STNG132 | STNG132T2 | 6.5205 | STNG132 132.00 | T2 | STNG132 | STNG132T2 | 6.5205 | 75120
[12 empty] | 75126 | TKLG132 132.00 | T1 | TKLG132 | TKLG132T1 | 3.6097 | TKLG132 132.00 | T1 | TKLG132 | TKLG132T1 | 3.6097 | 75126
[12 empty] | 75126 | TKLG132 132.00 | T2 | TKLG132 | TKLG132T2 | 3.6087 | TKLG132 132.00 | T2 | TKLG132 | TKLG132T2 | 3.6087 | 75126
[12 empty] | 75126 | TKLG132 132.00 | T3 | TKLG132 | TKLG132T3 | 18.7373 | TKLG132 132.00 | T3 | TKLG132 | TKLG132T3 | 18.7373 | 75126
[12 empty] | 75126 | TKLG132 132.00 | T4 | TKLG132 | TKLG132T4 | 18.7881 | TKLG132 132.00 | T4 | TKLG132 | TKLG132T4 | 18.7881 | 75126
[12 empty] | 75133 | GMSG132 132.00 | T1 | GMSG132 | GMSG132T1 | 5.9769 | GMSG132 132.00 | T1 | GMSG132 | GMSG132T1 | 5.9769 | 75133
[12 empty] | 75133 | GMSG132 132.00 | T2 | GMSG132 | GMSG132T2 | 5.9489 | GMSG132 132.00 | T2 | GMSG132 | GMSG132T2 | 5.9489 | 75133
[12 empty] | 75133 | GMSG132 132.00 | T3 | GMSG132 | GMSG132T3 | 6.2378 | GMSG132 132.00 | T3 | GMSG132 | GMSG132T3 | 6.2378 | 75133
[12 empty] | 75133 | GMSG132 132.00 | T4 | GMSG132 | GMSG132T4 | 6.2451 | GMSG132 132.00 | T4 | GMSG132 | GMSG132T4 | 6.2451 | 75133
[12 empty] | 75206 | JELI275 275.00 | T1 | JELI275 | JELI275T1 | 6.3818 | JELI275 275.00 | T1 | JELI275 | JELI275T1 | 6.3818 | 75206
[12 empty] | 75206 | JELI275 275.00 | T2 | JELI275 | JELI275T2 | 6.1705 | JELI275 275.00 | T2 | JELI275 | JELI275T2 | 6.1705 | 75206
[12 empty] | 75112 | KBRU132 132.00 | T1 | KBRU132 | KBRU132T1 | 25.5758 | KBRU132 132.00 | T1 | KBRU132 | KBRU132T1 | 25.5758 | 75112
[12 empty] | 75112 | KBRU132 132.00 | T2 | KBRU132 | KBRU132T2 | 15.169 | KBRU132 132.00 | T2 | KBRU132 | KBRU132T2 | 15.169 | 75112
[12 empty] | 75112 | KBRU132 132.00 | T3 | KBRU132 | KBRU132T3 | 24.9265 | KBRU132 132.00 | T3 | KBRU132 | KBRU132T3 | 24.9265 | 75112
[12 empty] | 75112 | KBRU132 132.00 | T4 | KBRU132 | KBRU132T4 | 8.5346 | KBRU132 132.00 | T4 | KBRU132 | KBRU132T4 | 8.5346 | 75112
[12 empty] | 75112 | KBRU132 132.00 | T5 | KBRU132 | KBRU132T5 | 24.9814 | KBRU132 132.00 | T5 | KBRU132 | KBRU132T5 | 24.9814 | 75112
[12 empty] | 75131 | KDIS132 132.00 | T1 | KDIS132 | KDIS132T1 | 17.123 | KDIS132 132.00 | T1 | KDIS132 | KDIS132T1 | 17.123 | 75131
[12 empty] | 75131 | KDIS132 132.00 | T2 | KDIS132 | KDIS132T2 | 17.0764 | KDIS132 132.00 | T2 | KDIS132 | KDIS132T2 | 17.0764 | 75131
[12 empty] | 75113 | KKRI132 132.00 | T1 | KKRI132 | KKRI132T1 | 8.8556 | KKRI132 132.00 | T1 | KKRI132 | KKRI132T1 | 8.8556 | 75113
[12 empty] | 75113 | KKRI132 132.00 | T2 | KKRI132 | KKRI132T2 | 8.7935 | KKRI132 132.00 | T2 | KKRI132 | KKRI132T2 | 8.7935 | 75113
[12 empty] | 75132 | LMAL132 132.00 | T1 | LMAL132 | LMAL132T1 | 38.8219 | LMAL132 132.00 | T1 | LMAL132 | LMAL132T1 | 38.8219 | 75132
[12 empty] | 75132 | LMAL132 132.00 | T2 | LMAL132 | LMAL132T2 | 38.4885 | LMAL132 132.00 | T2 | LMAL132 | LMAL132T2 | 38.4885 | 75132
[12 empty] | 75947 | MALS_LSS2 33.000 | X1 | MALS_LS | MALS_LSX1 | 0 | MALS_LSS2 33.000 | X1 | MALS_LS | MALS_LSX1 | 0 | 75947
[12 empty] | 75129 | PCOR132 132.00 | T2 | PCOR132 | PCOR132T2 | 38.9658 | PCOR132 132.00 | T2 | PCOR132 | PCOR132T2 | 38.9658 | 75129
[12 empty] | 75129 | PCOR132 132.00 | T3 | PCOR132 | PCOR132T3 | 32.9402 | PCOR132 132.00 | T3 | PCOR132 | PCOR132T3 | 32.9402 | 75129
[12 empty] | 75129 | PCOR132 132.00 | T4 | PCOR132 | PCOR132T4 | 29.6256 | PCOR132 132.00 | T4 | PCOR132 | PCOR132T4 | 29.6256 | 75129
[12 empty] | 75208 | PGAU275 275.00 | N1 | PGAU275 | PGAU275N1 | 0 | PGAU275 275.00 | N1 | PGAU275 | PGAU275N1 | 0 | 75208
[12 empty] | 75208 | PGAU275 275.00 | N2 | PGAU275 | PGAU275N2 | 0 | PGAU275 275.00 | N2 | PGAU275 | PGAU275N2 | 0 | 75208
[12 empty] | 75114 | PPTH132 132.00 | T1 | PPTH132 | PPTH132T1 | 19.6103 | PPTH132 132.00 | T1 | PPTH132 | PPTH132T1 | 19.6103 | 75114
[12 empty] | 75114 | PPTH132 132.00 | T2 | PPTH132 | PPTH132T2 | 19.1226 | PPTH132 132.00 | T2 | PPTH132 | PPTH132T2 | 19.1226 | 75114
[12 empty] | 75134 | RPJG132 132.00 | T1 | RPJG132 | RPJG132T1 | 6.3259 | RPJG132 132.00 | T1 | RPJG132 | RPJG132T1 | 6.3259 | 75134
[12 empty] | 75134 | RPJG132 132.00 | T2 | RPJG132 | RPJG132T2 | 6.1819 | RPJG132 132.00 | T2 | RPJG132 | RPJG132T2 | 6.1819 | 75134
[12 empty] | 75106 | SJTH132 132.00 | T1 | SJTH132 | SJTH132T1 | 21.3261 | SJTH132 132.00 | T1 | SJTH132 | SJTH132T1 | 21.3261 | 75106
[12 empty] | 75106 | SJTH132 132.00 | T2 | SJTH132 | SJTH132T2 | 21.5291 | SJTH132 132.00 | T2 | SJTH132 | SJTH132T2 | 21.5291 | 75106
[12 empty] | 75106 | SJTH132 132.00 | T5 | SJTH132 | SJTH132T5 | 14.8915 | SJTH132 132.00 | T5 | SJTH132 | SJTH132T5 | 14.8915 | 75106
[12 empty] | 75127 | TJUG132 132.00 | T1 | TJUG132 | TJUG132T1 | 26.6216 | TJUG132 132.00 | T1 | TJUG132 | TJUG132T1 | 26.6216 | 75127
[12 empty] | 75127 | TJUG132 132.00 | T2 | TJUG132 | TJUG132T2 | 30.4043 | TJUG132 132.00 | T2 | TJUG132 | TJUG132T2 | 30.4043 | 75127
[12 empty] | 75101 | TMRH132 132.00 | T1 | TMRH132 | TMRH132T1 | 0 | TMRH132 132.00 | T1 | TMRH132 | TMRH132T1 | 0 | 75101
[12 empty] | 75101 | TMRH132 132.00 | T2 | TMRH132 | TMRH132T2 | 33.809 | TMRH132 132.00 | T2 | TMRH132 | TMRH132T2 | 33.809 | 75101
[12 empty] | 75101 | TMRH132 132.00 | T3 | TMRH132 | TMRH132T3 | 34.0472 | TMRH132 132.00 | T3 | TMRH132 | TMRH132T3 | 34.0472 | 75101
[12 empty] | 61103 | TEWA132 132.00 | T1 | TEWA132 | TEWA132T1 | 0 | TEWA132 132.00 | T1 | TEWA132 | TEWA132T1 | 0 | 61103
[12 empty] | 61103 | TEWA132 132.00 | T2 | TEWA132 | TEWA132T2 | 33.2882 | TEWA132 132.00 | T2 | TEWA132 | TEWA132T2 | 33.2882 | 61103
[12 empty] | 61125 | UMKA132 132.00 | T1 | UMKA132 | UMKA132T1 | 3.7268 | UMKA132 132.00 | T1 | UMKA132 | UMKA132T1 | 3.7268 | 61125
[12 empty] | 61125 | UMKA132 132.00 | T2 | UMKA132 | UMKA132T2 | 3.7237 | UMKA132 132.00 | T2 | UMKA132 | UMKA132T2 | 3.7237 | 61125
[12 empty] | 61125 | UMKA132 132.00 | T3 | UMKA132 | UMKA132T3 | 17.299 | UMKA132 132.00 | T3 | UMKA132 | UMKA132T3 | 17.299 | 61125
[12 empty] | 61125 | UMKA132 132.00 | T4 | UMKA132 | UMKA132T4 | 17.1541 | UMKA132 132.00 | T4 | UMKA132 | UMKA132T4 | 17.1541 | 61125
[12 empty] | 96141 | SHEL132 132.00 | F1 | SHEL132 | SHEL132F1 | 18.1541 | SHEL132 132.00 | F1 | SHEL132 | SHEL132F1 | 18.1541 | 96141
[12 empty] | 96141 | SHEL132 132.00 | F2 | SHEL132 | SHEL132F2 | 19.1541 | SHEL132 132.00 | F2 | SHEL132 | SHEL132F2 | 19.1541 | 96141
[12 empty] | 96193 | SSUN132 132.00 | T3 | SSUN132 | SSUN132T3 | 0 | SSUN132 132.00 | T3 | SSUN132 | SSUN132T3 | 0 | 96193
[12 empty] | 96193 | SSUN132 132.00 | T4 | SSUN132 | SSUN132T4 | 0 | SSUN132 132.00 | T4 | SSUN132 | SSUN132T4 | 0 | 96193
[12 empty] | 96193 | SSUN132 132.00 | T5 | SSUN132 | SSUN132T5 | 0 | SSUN132 132.00 | T5 | SSUN132 | SSUN132T5 | 0 | 96193
[12 empty] | 596193 | SSUN132N 132.00 | T1 | SSUN132 | SSUN132T1 | 18.5282 | SSUN132N 132.00 | T1 | SSUN132 | SSUN132T1 | 18.5282 | 596193
[12 empty] | 596193 | SSUN132N 132.00 | T2 | SSUN132 | SSUN132T2 | 19.2717 | SSUN132N 132.00 | T2 | SSUN132 | SSUN132T2 | 19.2717 | 596193
[12 empty] | 96151 | NSCI132 132.00 | T1 | NSCI132 | NSCI132T1 | 12.6745 | NSCI132 132.00 | T1 | NSCI132 | NSCI132T1 | 12.6745 | 96151
[12 empty] | 96151 | NSCI132 132.00 | T2 | NSCI132 | NSCI132T2 | 13.5692 | NSCI132 132.00 | T2 | NSCI132 | NSCI132T2 | 13.5692 | 96151
[12 empty] | 96124 | XNYI132 132.00 | F1 | XNYI132 | XNYI132F1 | 9.9734 | XNYI132 132.00 | F1 | XNYI132 | XNYI132F1 | 9.9734 | 96124
[12 empty] | 96124 | XNYI132 132.00 | F2 | XNYI132 | XNYI132F2 | 27.8171 | XNYI132 132.00 | F2 | XNYI132 | XNYI132F2 | 27.8171 | 96124
[12 empty] | 74147 | MNID132 132.00 | F1 | MNID132 | MNID132F1 | 0.321 | MNID132 132.00 | F1 | MNID132 | MNID132F1 | 0.321 | 74147
[12 empty] | 96181 | SPWR132 132.00 | F1 | SPWR132 | SPWR132F1 | 1.321 | SPWR132 132.00 | F1 | SPWR132 | SPWR132F1 | 1.321 | 96181
[12 empty] | 96181 | SPWR132 132.00 | F2 | SPWR132 | SPWR132F2 | 2.321 | SPWR132 132.00 | F2 | SPWR132 | SPWR132F2 | 2.321 | 96181
[12 empty] | 96181 | SPWR132 132.00 | F3 | SPWR132 | SPWR132F3 | 3.321 | SPWR132 132.00 | F3 | SPWR132 | SPWR132F3 | 3.321 | 96181
[12 empty] | 96197 | PPSR132 132.00 | F1 | PPSR132 | PPSR132F1 | 2.7441 | PPSR132 132.00 | F1 | PPSR132 | PPSR132F1 | 3.321 | 96197
[12 empty] | 96197 | PPSR132 132.00 | F2 | PPSR132 | PPSR132F2 | 0.1243 | PPSR132 132.00 | F2 | PPSR132 | PPSR132F2 | 3.321 | 96197
[12 empty] | 96196 | HLNM132 132.00 | F1 | HLNM132 | HLNM132F1 | 9.539 | HLNM132 132.00 | F1 | HLNM132 | HLNM132F1 | 9.539 | 96196
[12 empty] | 97159 | UTMJ132 132.00 | F1 | UTMJ132 | UTMJ132F1 | 4.0799 | UTMJ132 132.00 | F1 | UTMJ132 | UTMJ132F1 | 4.0799 | 97159
[12 empty] | 597159 | UTMJ132R 132.00 | F2 | UTMJ132R | UTMJ132RF2 | 1.3565 | UTMJ132R 132.00 | F2 | UTMJ132R | UTMJ132RF2 | 1.3565 | 597159
[12 empty] | 62126 | JNKO132 132.00 | F1 | JNKO132 | JNKO132F1 | 0.3334 | JNKO132 132.00 | F1 | JNKO132 | JNKO132F1 | 0.3334 | 62126
[12 empty] | 62126 | JNKO132 132.00 | F2 | JNKO132 | JNKO132F2 | 0.0332 | JNKO132 132.00 | F2 | JNKO132 | JNKO132F2 | 0.0332 | 62126
[12 empty] | 96194 | HLNN132 132.00 | F1 | HLNN132 | HLNN132F1 | 0.1118 | HLNN132 132.00 | F1 | HLNN132 | HLNN132F1 | 0.1118 | 96194
[12 empty] | 96194 | HLNN132 132.00 | F2 | HLNN132 | HLNN132F2 | 10.7143 | HLNN132 132.00 | F2 | HLNN132 | HLNN132F2 | 10.7143 | 96194
[12 empty] | 96194 | HLNN132 132.00 | F3 | HLNN132 | HLNN132F3 | 10.8686 | HLNN132 132.00 | F3 | HLNN132 | HLNN132F3 | 10.8686 | 96194
[12 empty] | 96194 | HLNN132 132.00 | F4 | HLNN132 | HLNN132F4 | 0 | HLNN132 132.00 | F4 | HLNN132 | HLNN132F4 | 0 | 96194
[12 empty] | 61145 | KCMT132 132.00 | F1 | KCMT132 | KCMT132F1 | 0 | KCMT132 132.00 | F1 | KCMT132 | KCMT132F1 | 0 | 61145
[12 empty] | 561145 | KCMT132R 132.00 | F2 | KCMT132R | KCMT132RF2 | 26.1764 | KCMT132R 132.00 | F2 | KCMT132R | KCMT132RF2 | 26.1764 | 561145