## ufls
2025_Assignment | 2024_Assignment | GM_Subzone | Geo_Region | Substation | Mnemonic | kV | Assigned_Feeders | CB | Freq1 | Delay1 (s) | Freq2 | Delay2 (s) | Group_id | MW Quantum 2024 | Load_Area | Remarks
| Stage: Ride Through | East-Kuantan |  | Gebeng Industri | GBID | 132 | KSTL 1 & 2 | 105 & 405 | 49.3 | 0 | n/a | n/a |  | 0 | KSTL load | Defeated - No more in business. Physical jumper has been removed
| Stage: Ride Through | South-JB | Johor | Tanjung Langsat | TLST | 132 | TLTP (Titan Petrochemicals) | 505 | 49.3 | 0 | n/a | n/a |  | 26 | TLTP
| Stage: Ride Through | South-JB | Johor | Pasir Gudang Darat | PGDT | 132 | TTAN 1 & 2 | 905 & 1005 | 49.3 | 0 | n/a | n/a |  | 28 | TTAN
| Stage: Ride Through | South-JB | Johor | Pasir Gudang Ind Est | PGIE | 132 | ASTM 1 & 2 | 805 & 905 | 49.3 | 0 | n/a | n/a |  | 2 | ASTM
| Stage: Ride Through | South-JB | Johor | Tanjung Langsat Industrial Estate | TLIE | 275 | BSTL 1 & 2 | L15 & L25 | 49.3 | 0 | n/a | n/a |  | 7 | BSTL
| Stage: Ride Through | East-Kuantan | Pahang | Tanjung Gelang | TGLN | 132 | JDSI 1 & 2 | 505 & 605 | 49.3 | 0 | n/a | n/a |  | 0 | JDSI
| Stage: Ride Through | East-Dungun | Kelantan-Terengganu | Telok Kalong | TKLG | 275 | Perwaja 1 & 2 | L15 & L25 | 49.3 | 1 | n/a | n/a |  | 0 | PWSM
| Stage: Ride Through | Selangor | KlangValley | Olak Lempit | OLPT | 275 | MGST 1 & 2 | L75 & L85 | 49.3 | 0 | n/a | n/a |  | 25 | MGST
| Stage: Ride Through | Selangor | KlangValley | Bukit Raja GIS | BRGS | 132 | ASMB 1 & 2 | 11130, 11230, 11330 | 49.3 | 0 | n/a | n/a |  | 44 | ASMB
| Stage: Ride Through | Selangor | KlangValley | Bukit Raja GIS | BRGS | 132 | MSWK | 7130, 7230 | 49.3 | 0 | n/a | n/a |  | 60 | MSWK
| Stage: Ride Through | North-Perda | Penang | Bukit Tengah | BTGH | 132 | SRON 2 | 905 | 49.3 | 0 | n/a | n/a |  | 50 | SRON 905 only
| Stage: Ride Through | North-Perda | Kedah-Perlis | Bedong | BDNG | 275 | PWGR 1 & 2 feeders | L35 & L45 | 49.3 | 0 | n/a | n/a |  | 6 | PWGR
| Stage: Ride Through | North-Perda | Penang | Prai Industrial | PRID | 132 | SRON & SRNW | 505 & 605 | 49.3 | 0 | n/a | n/a |  | 17 | SRON & SRNW
| Stage: Ride Through | North-Perda | Penang | SKS Prai | SKSP | 132 | MWTA 1 & 2 | 105 & 205 | 49.3 | 0 | n/a | n/a |  | 46 | MWTA
Stage 1: 49.0Hz | Stage 3: 49.0Hz | KL | KlangValley | Balakong | BLKG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a |  | 52.1303 | BLKG 33 kV
| Stage 3: 49.0Hz | KL | KlangValley | Serdang Raya | SRDR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a |  | 85.1885 | SRDR 33kV
| Stage 5: 48.8Hz | KL | KlangValley | Kg Chempaka | KCPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a |  | 71.7948 | KCPK 33kV
| Stage 6: 48.7Hz | Selangor | KlangValley | Rasa Selangor Industry | RSID | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a |  | 31.7609 | RSID 11kV
| Stage 5: 48.8Hz | Selangor | KlangValley | Bukit Kapar | BKPR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a |  | 69.4631 | BKPR 33kV
| Stage 7: 48.6Hz | Selangor | KlangValley | Teluk Panglima Garang | TPGR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a |  | 98.751 | TPGR 33kV
| Stage 4: 48.9Hz | South-N9 | Melaka-N9 | Sendayan | SDYN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a |  | 64.8369 | SDYN 33kV
| Stage 6: 48.7Hz | South-N9 | Melaka-N9 | Nilai | NLAI | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a |  | 22.8675 | NLAI 11kV
| Stage 3: 49.0Hz | South-Melaka | Johor | Muar | MUAR | 11 | 132/11kV T2 & T3 | 32 & 33 | 49 | 0 | n/a | n/a |  | 32.3916 | MUAR 11kV
| Stage 1: 49.2Hz | South-JB | Johor | Cahaya Baru | CBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 21.3659 | CBRU 22kV
| Stage 1: 49.2Hz | South-JB | Johor | Pasir Gudang Darat | PGDT | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 21.8789 | PGDT 22kV
| Stage 1: 49.2Hz | South-JB | Johor | Tampoi Industries | TMPI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 64.0768 | TMPI 33kV
| Stage 1: 49.2Hz | North-Perda | Penang | Sungai Ara (GIS) | SARA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 41.5461 | SARA 33kV | to remove - proposed by DN
| Stage 1: 49.2Hz | East-Kuantan | Pahang | Pekan Industri AIP | PKNI | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a |  | 18.5562 | PKNI 33kV
| Stage 1: 49.2Hz | South-Melaka | Melaka-N9 | Hicom Pegoh | HPGH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 15.3861 | HPGH 33kV
| Stage 1: 49.2Hz | South-N9 | Melaka-N9 | Enstek | ESTK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 36.4197 | ESTK 33kV
| Stage 1: 49.2Hz | South-N9 | Melaka-N9 | Kg. Repah | KRPH | 11 | 132/11kV T1 & T2 | 30 & 32 | 49.2 | 0 | n/a | n/a |  | 20.2233 | KRPH 11kV | to remove - proposed by DN
| Stage 1: 49.2Hz | North-Ipoh | Perak | Pengkalan Industri | PKID | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a |  | 21.5372 | PKID 11kV
| Stage 1: 49.2Hz | North-Ipoh | Perak | Pengkalan Industri | PKID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a |  | 25.2821 | PKID 33kV
| Stage 1: 49.2Hz | North-Ipoh | Perak | Kinta Valley Resort | KVRT | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.2 | 0 | n/a | n/a |  | 61.5771 | KVRT 33 kV
| Stage 1: 49.2Hz | North-Ipoh | Perak | Menglembu | MLBU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a |  | 83.9211 | MLBU 33kV | to remove - proposed by DN
| Stage 1: 49.2Hz | Selangor | KlangValley | Setia Alam | STIA | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a |  | 76.0234 | STIA 33kV
| Stage 1: 49.2Hz | KL | KlangValley | Damansara City | DCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 28.4475 | DCTY 33kV
| Stage 1: 49.2Hz | KL | KlangValley | Manjalara | MJLR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 89.8683 | MJLR 33kV
| Stage 1: 49.2Hz | KL | KlangValley | Sri Hartamas | SHMS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 71.0055 | SHMS 33kV | Removed (15 Oct 2025) - load to Istana Negara
| Stage 1: 49.2Hz | KL | KlangValley | Suncity GIS | SCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T2 | 49.2 | 0 | n/a | n/a |  | 25.6995 | SCTY 33kV | Removed (15 Oct 2025) - load to TRX
| Stage 1: 49.2Hz | KL | KlangValley | Cheras Jaya | CJYA | 33 | 132/33kV T1, T2 & T3 | 1T0 & 2T0 & 3T0 | 49.2 | 0 | n/a | n/a |  | 157.1371 | CJYA 33kV
| Stage 1: 49.2Hz | KL | KlangValley | Danau Desa | DDSA | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a |  | 60.7924 | DDSA 33kV | to remove - proposed by DN
| Stage 1: 49.2Hz | North-Kedah_Perlis | Kedah-Perlis | Mergong | MGON | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a |  | 17.2107 | MGON 11kV | to remove - proposed by DN
| Stage 1: 49.2Hz | North-Kedah_Perlis | Kedah-Perlis | Pauh | PAUH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a |  | 42.691 | PAUH 33kV
| Stage 2: 49.1Hz | North-Ipoh | Perak | Temoh | TMOH | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.1 | 0 | n/a | n/a |  | 22.3732 | TMOH 33kV
| Stage 2: 49.1Hz | North-Ipoh | Perak | Kelebang | KLBG | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.1 | 0 | n/a | n/a |  | 24.6724 | KLBG 33kV
| Stage 2: 49.1Hz | North-Ipoh | Perak | New Khantan | NKAN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a |  | 32.1433 | NKAN 33kV
| Stage 2: 49.1Hz | North-Ipoh | Perak | Tasik | TASK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a |  | 8.5343 | TASK 22kV
| Stage 2: 49.1Hz | KL | KlangValley | SPPK Cheras | SPKC | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 1W0 & 5T0 | 49.1 | 0 | n/a | n/a |  | 123.2475 | SPKC 33kV
| Stage 2: 49.1Hz | KL | KlangValley | National University | NUNI | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a |  | 24.5161 | NUNI 11kV
| Stage 2: 49.1Hz | South-JB | Johor | Plentong | PLTG | 230 | WA18 1 & 2 | H10 & H20 | 49.1 | 0 | n/a | n/a |  | - | TNB-Singapore Interconnection
| Stage 2: 49.1Hz | South-JB | Johor | Tebrau | TBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a |  | 29.3428 | TBRU 22kV
| Stage 2: 49.1Hz | East-Kuantan | Pahang | Kampung Awah | KAWA | 132 | KRYG 1 & 2 | 305 & 405 | 49.1 | 0 | n/a | n/a |  | 30 | KRYG
| Stage 2: 49.1Hz | South-N9 | Melaka-N9 | Tuanku Jaafar (GIS) | TJGS | 132 | SHEL 1 & 2 | 505 & 605 | 49.1 | 0 | n/a | n/a |  | 36 | SHELL
| Stage 2: 49.1Hz | Selangor | KlangValley | Hicom | HCOM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a |  | 77.918 | HCOM 33 kV
| Stage 2: 49.1Hz | Selangor | KlangValley | Shah Alam East | SHAE | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 49.1 | 0 | n/a | n/a |  | 72.8698 | SHAE 33kV
| Stage 2: 49.1Hz | Selangor | KlangValley | Shah Alam South | SHAS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a |  | 64 | SHAS 33kV
| Stage 2: 49.1Hz | East-KB | Kelantan-Terengganu | Panchor | PCOR | 33 | 132/33kV T2 & T3 & T4 | 2T0, 3T0 & 4T0 | 49.1 | 0 | n/a | n/a |  | 67.9031 | PCOR 33kV | to remove - proposed by DN
| Stage 2: 49.1Hz | South-Kluang | Johor | Johor Tengah | JTGH | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a |  | 20.2863 | JTGH 11kV
| Stage 2: 49.1Hz | North-Perda | Penang | Seberang Jaya | SJAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a |  | 74.3213 | SJAY 33kV | to remove - proposed by DN
| Stage 2: 49.1Hz | North-Perda | Kedah-Perlis | Taman Intan | INTN | 33 | 132/33kV T3 & T4 | 3T0&4T0 | 49.1 | 0 | n/a | n/a |  | 51.9714 | INTN 33kV
| Stage 2: 49.1Hz | North-Perda | Kedah-Perlis | Taman Intan | INTN | 11 | 132/11kV T1 & T2 | 31&32 | 49.1 | 0 | n/a | n/a |  | 31.6547 | INTN 22kV
| Stage 2: 49.1Hz | South-Melaka | Melaka-N9 | Malacca Power Station | MPSS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a |  | 9.404 | MPSS 11kV
| Stage 3: 49.0Hz | East-KB | Kelantan-Terengganu | Tunjung | TJUG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a |  | 60 | TJUG 33kV
| Stage 3: 49.0Hz | South-Melaka | Melaka-N9 | Malim Jaya | MJYA | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a |  | 26.877 | MJYA 11kV
| Stage 3: 49.0Hz | Selangor | KlangValley | Bukit Rajah | BRGS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a |  | 18.9852 | BRGS 11 kV
| Stage 3: 49.0Hz | Selangor | KlangValley | Port Klang P/S | PKLG | 132 | IGBK 1 & 2 | 705 & 805 | 49 | 0 | n/a | n/a |  | 130 | IGBK & NKST
| Stage 3: 49.0Hz | Selangor | KlangValley | Bukit Beruntung | BBTG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a |  | 41.8364 | BBTG 33kV
| Stage 3: 49.0Hz | East-Kuantan | Pahang | Bandar Indra Mahkota | BIMK | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a |  | 28.0406 | BIMK 11kV | to remove - proposed by DN
| Stage 3: 49.0Hz | East-Kuantan | Pahang | Bandar Indra Mahkota | BIMK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a |  | 98.0819 | BIMK 33kV | to remove - proposed by DN
| Stage 3: 49.0Hz | East-Kuantan | Pahang | Bentong | BNTG | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a |  | 23.208 | BNTG 11kV
| Stage 3: 49.0Hz | North-Perda | Penang | Butterworth North | BWTN | 33 | 132/33 kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a |  |  | BWTN 33kV
| Stage 3: 49.0Hz | North-Perda | Penang | Butterworth North | BWTN | 11 | 132/11kV T5 | 35 | 49 | 0 | n/a | n/a |  |  | BWTN 11kV
| Stage 3: 49.0Hz | North-Perda | Penang | Prai GIS | PRGS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a |  | 61.6121 | PRGS 33 kV
| Stage 3: 49.0Hz | KL | KlangValley | Ampang GIS | AMPG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a |  | 75.8672 | AMPG T3&T4 | to remove - proposed by DN
| Stage 3: 49.0Hz | KL | KlangValley | Air Hitam | AHTM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a |  | 65.0735 | AHTM 33kV | to remove - proposed by DN
| Stage 3: 49.0Hz | KL | KlangValley | Bukit Jalil | BJLL | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a |  | 85.6804 | BJLL 33kV
| Stage 4: 48.9Hz | East-KB | Kelantan-Terengganu | Kota Bharu | KBRU | 33 | 132/33kV T1 & T3 & T5 | 1T0 & 3T0 & 5T0 | 48.9 | 0 | n/a | n/a |  | 82.5745 | KBRU 33kV
| Stage 4: 48.9Hz | Selangor | KlangValley | PJ Selatan | PJST | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a |  | 65.7207 | PJST 33 kV
| Stage 4: 48.9Hz | South-Kluang | Johor | Pasir Gudang Town Centre | PGTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a |  | 111.1269 | PGTC 33kV
| Stage 4: 48.9Hz | South-JB | Johor | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a |  | 37.2708 | PGIE 22kV
| Stage 4: 48.9Hz | South-JB | Johor | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T3 | 3T0 | 48.9 | 0 | n/a | n/a |  | 15.0562 | PGIE 22kV
| Stage 4: 48.9Hz | Selangor | KlangValley | Puchong Jaya | PCHJ | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a |  | 83.0514 | PCHJ 33kV
| Stage 4: 48.9Hz | Selangor | KlangValley | New Subang Uda | NSDA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a |  | 62.5762 | NSDA 33 kV
| Stage 4: 48.9Hz | KL | KlangValley | Sri Damansara | SDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a |  | 67.9905 | SDAM 33kV | to remove - proposed by DN
| Stage 4: 48.9Hz | KL | KlangValley | New SEA Park | NSPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a |  | 68.1678 | NSPK 33 kV | to remove - proposed by DN
| Stage 4: 48.9Hz | KL | KlangValley | Serdang New | SRDN | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.9 | 0 | n/a | n/a |  | 51.941 | SRDN 33kV | to remove - proposed by DN
| Stage 4: 48.9Hz | South-N9 | Melaka-N9 | Lukut | LKUT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.9 | 0 | n/a | n/a |  | 17.6596 | LKUT 11kV
| Stage 4: 48.9Hz | East-Kuantan | Pahang | Tanjong Gelang | TGLN | 11 | 132/11kV T1 & T2 & T3 | 31 & 32 & 33 | 48.9 | 0 | n/a | n/a |  | 25.8429 | TGLN 11kV
| Stage 5: 48.8Hz | North-Kedah_Perlis | Kedah-Perlis | Kota Setar | KSTR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a |  | 25.7531 | KSTR 11kV
| Stage 5: 48.8Hz | Selangor | KlangValley | New Rawang | NRWG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a |  | 74.945 | NRWG 33 kV
| Stage 5: 48.8Hz | Selangor | KlangValley | Temasya | TMSY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a |  | 60.1524 | TMSY 33 kV | to remove - proposed by DN
| Stage 5: 48.8Hz | South-Melaka | Melaka-N9 | Kelemak | KLMK | 132 | MTNH 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | klmk_rtau | 49 | TKMG, PPJG, MTNH
| Stage 5: 48.8Hz | South-N9 | Melaka-N9 | Rantau | RTAU | 132 | TKMG 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | klmk_rtau
| Stage 5: 48.8Hz | South-N9 | Melaka-N9 | Paroi | PROI | 132 | TJID 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a | proi_rasa_ | 140 | TJID, TTJF, SSUN & STRA
| Stage 5: 48.8Hz | South-N9 | Melaka-N9 | Rasah | RASA | 132 | Satria & TTJF | 505 & 605 | 48.8 | 0 | n/a | n/a | proi_rasa_ |  |  | to remove - proposed by DN
| Stage 5: 48.8Hz | East-Kuantan | Pahang | Bentong South | BNTS | 132 | BNTG & RBDR | 205 & 405 | 48.8 | 0 | n/a | n/a | bnts_kawa | 133 | BNTA, KLIP, JNKA, JTUT, RBDR
| Stage 5: 48.8Hz | East-Kuantan | Pahang | Kg. Awah | KAWA | 132 | JNKA & JTUT | 205 & 705 | 48.8 | 0 | n/a | n/a | bnts_kawa
| Stage 5: 48.8Hz | North-Perda | Penang | Air terjun | ATJN | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a |  | 56.7503 | ATJN 33 kV | to remove - proposed by DN
| Stage 5: 48.8Hz | North-Perda | Kedah-Perlis | Gurun | GRUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a |  | 9.3912 | GRUN 11kV
| Stage 5: 48.8Hz | North-Perda | Kedah-Perlis | Jeniang | JENG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a |  | 22.7999 | JENG 33kV
| Stage 6: 48.7Hz | North-Ipoh | Perak | Lumut | LMUT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a |  | 58.1226 | LMUT 33kV | to remove - proposed by DN
| Stage 6: 48.7Hz | North-Ipoh | Perak | Lumut Maritime | LMTM | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a |  | 72.3964 | LMTM 33kV | to remove - proposed by DN
| Stage 6: 48.7Hz | KL | KlangValley | Mutiara Damansara | MDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a |  | 38.9019 | MDAM 33kV
| Stage 6: 48.7Hz | KL | KlangValley | Batu Caves | BCVS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a |  | 84.9599 | BCVS 33kV
| Stage 6: 48.7Hz | South-Kluang | Johor | Parit Raja | PRJA | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a |  | 17.3238 | PRJA 11kV
| Stage 6: 48.7Hz | South-Kluang | Johor | Yong Peng North | YGPN | 132 | CAAH & BSPT/BKPG | 105 & 205 | 48.7 | 0 | n/a | n/a | ygpn_proi_lkjg | 298 | LKJG, XNSS, XNYI, TKID, TKAK, JMTH, SGMT, BSPT, BKPG, CAAH, BAHA, NSCI, GMAS, PBSR, KLPH, SPTG, KKWG | to remove - proposed by DN
| Stage 6: 48.7Hz | South-N9 | Melaka-N9 | Paroi | PROI | 132 | KPLH 1 & 2 | 705 & 805 | 48.7 | 0 | n/a | n/a | ygpn_proi_lkjg |  |  | to remove - proposed by DN
| Stage 6: 48.7Hz | South-Melaka | Melaka-N9 | Lipat Kajang | LKJG | 132 | JSIN & MCOP | 505 & 605 | 48.7 | 0 | n/a | n/a | ygpn_proi_lkjg |  |  | to remove - proposed by DN
| Stage 6: 48.7Hz | South-Melaka | Melaka-N9 | Ujong Pasir | UPSR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a |  | 18 | UPSR 11kV
| Stage 6: 48.7Hz | South-Melaka | Melaka-N9 | Ujong Pasir | UPSR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a |  | 60 | UPSR 33kV | to remove - proposed by DN
| Stage 6: 48.7Hz | South-Melaka | Melaka-N9 | Metacorp | MCOP | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a |  | 30 | MCOP 11kV | to remove - proposed by DN
| Stage 6: 48.7Hz | South-Melaka | Melaka-N9 | Metacorp | MCOP | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a |  | 61 | MCOP 33kV
| Stage 6: 48.7Hz | Selangor | KlangValley | Batu Tiga | BTGA | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.7 | 0 | n/a | n/a |  | 71.3972 | BTGA 33kV
| Stage 6: 48.7Hz | Selangor | KlangValley | Bukit Badong | BBDG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a |  | 66.6988 | BBDG 33kV
| Stage 7: 48.6Hz | South-Melaka | Johor | Gerisik | GRSK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a |  | 21.3927 | GRSK 11kV
| Stage 7: 48.6Hz | South-JB | Johor | Kota Putri | KPTR | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a |  | 35.0813 | KPTR 22kV
| Stage 7: 48.6Hz | South-JB | Johor | Skudai | SDAI | 22 | 132/22kV T7 & T8 | 37 & 38 | 48.6 | 0 | n/a | n/a |  | 1.4469 | SDAI 22kV
| Stage 7: 48.6Hz | South-JB | Johor | Larkin GIS | LKIN | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a |  | 33.3325 | LKIN 22kV
| Stage 7: 48.6Hz | East-Kuantan | Pahang | Kg. Awah | KAWA | 132 | SONG | 605 | 48.6 | 0 | n/a | n/a | kawa_jbrs | 90 | SONG, MTKB, TMID, MNID
| Stage 7: 48.6Hz | East-Kuantan | Pahang | Jambu Rias | JBRS | 132 | TMID | 205 | 48.6 | 0 | n/a | n/a | kawa_jbrs
| Stage 7: 48.6Hz | North-Perda | Penang | Gelugor | GLGR | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.6 | 0 | n/a | n/a |  | 61.1334 | GLGR 33kV
| Stage 7: 48.6Hz | North-Perda | Penang | Bayan Mutiara | BMTR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a |  | 105.8642 | BMTR 33kV
| Stage 7: 48.6Hz | North-Perda | Penang | Batu Kawan South | BTWS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a |  | 52.4377 | BTWS 33kV
| Stage 7: 48.6Hz | North-Kedah_Perlis | Kedah-Perlis | Kangar | KGAR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a |  | 14.2995 | KGAR 33kV
| Stage 7: 48.6Hz | Selangor | KlangValley | Shah Alam West | SHAW | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a |  | 69.0504 | SHAW 33kV
| Stage 7: 48.6Hz | Selangor | KlangValley | Shah Alam West | SHAW | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a |  | 15.0282 | SHAW 11kV
| Stage 7: 48.6Hz | Selangor | KlangValley | Shah Alam North | SHAN | 11 | 132/11kV T1, T2 & T3 | 31, 32 & 33 | 48.6 | 0 | n/a | n/a |  | 4.0549 | SHAN 11kV
| Stage 7: 48.6Hz | Selangor | KlangValley | Shah Alam Section 18 GIS | SHLB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a |  | 77.1695 | SHLB 33kV
| Stage 7: 48.6Hz | Selangor | KlangValley | Bandar Botanic | BBTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a |  | 81.8867 | BBTC 33kV
| Stage 7: 48.6Hz | North-Perda | Kedah-Perlis | Bedong | BDNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a |  | 45.0985 | BDNG 33kV
| Stage 7: 48.6Hz | KL | KlangValley | Kuala Lumpur North | KULN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a |  | 71.6655 | KULN 33kV
| Stage 7: 48.6Hz | East-Dungun | Kelantan-Terengganu | Dungun | DGUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a |  | 9.9042 | DGUN 11kV
| Stage 7: 48.6Hz | East-Dungun | Kelantan-Terengganu | Chendering | CHRG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a |  | 18.4411 | CHRG 11kV
| Stage 8: 48.5Hz | South-Kluang | Johor | Kluang (New) | KLUG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a |  | 20.3434 | KLUG 11kV
| Stage 8: 48.5Hz | South-JB | Johor | Majidee | MAJD | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a |  | 34.6464 | MAJD 22kV
| Stage 8: 48.5Hz | East-Dungun | Kelantan-Terengganu | Dungun Industries | DGID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a |  | 17.7645 | DGID 33kV
| Stage 8: 48.5Hz | East-Dungun | Kelantan-Terengganu | Chukai | CKAI | 33 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a |  | 16.51 | CKAI 11kV
| Stage 8: 48.5Hz | North-Kedah_Perlis | Kedah-Perlis | Tanjong Pauh | PAUH | 11 | 132/11kV T3 & T4 | 35 & 36 | 48.5 | 0 | n/a | n/a |  | 20.2035 | PAUH 11kV
| Stage 8: 48.5Hz | North-Perda | Penang | Bukit Minyak | BMYK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a |  | 40.4944 | BMYK 11kV
| Stage 8: 48.5Hz | North-Perda | Penang | Bukit Minyak | BMYK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a |  | 99.6068 | BMYK 33kV
| Stage 8: 48.5Hz | North-Perda | Penang | Prai Industries | PRID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a |  | 70.4984 | PRID 33kV
| Stage 8: 48.5Hz | North-Perda | Penang | Prai Industries | PRID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a |  | 99.1207 | PRID 33kV
| Stage 8: 48.5Hz | Selangor | KlangValley | Puchong Perdana | PCHP | 33 | 132/33kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.5 | 0 | n/a | n/a |  | 96.6747 | PCHP 33kV
| Stage 8: 48.5Hz | Selangor | KlangValley | Connaught Bridge PS | CBPS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a |  | 127.7547 | CBPS 33kV
| Stage 8: 48.5Hz | Selangor | KlangValley | Bandar Baru Shah Alam | SHAB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a |  | 90.9176 | SHAB 33kV
| Stage 8: 48.5Hz | KL | KlangValley | Segambut | SGBT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a |  | 81.4331 | SGBT 33kV
| Stage 8: 48.5Hz | East-KB | Kelantan-Terengganu | Jeli | JELI | 33 | 275/33kV T1 & T2 | 1T0 & 2T1 | 48.5 | 0 | n/a | n/a |  | 16.6814 | JELI 33kV
| Stage 8: 48.5Hz | East-KB | Kelantan-Terengganu | Tanah Merah | TMRH | 132 | Pasir Putih 1 & 2 | 305 & 405 | 48.5 | 0 | n/a | n/a | tmrh_kdis | 83 | PPTH & SJTH
| Stage 8: 48.5Hz | East-KB | Kelantan-Terengganu | Kandis | KDIS | 132 | Pasir Putih 1 & 2 | 505 & 605 | 48.5 | 0 | n/a | n/a | tmrh_kdis
| Stage 9: 48.4Hz | South-Melaka | Melaka-N9 | Kelemak | KLMK | 132 | CHNG & ZRNA | 305 & 805 | 48.4 | 0 | n/a | n/a | klmk_mjya_mcca | 268 | ZRNA, SPWR, CHNG, BMKA, MMKA, BVTA, MFDR, TGBU, PPSR, HLNM, BRBI
| Stage 9: 48.4Hz | South-Melaka | Melaka-N9 | Malim Jaya | MJYA | 132 | BVTA 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a | klmk_mjya_mcca
| Stage 9: 48.4Hz | South-Melaka | Melaka-N9 | Malacca | MCCA | 132 | BRBI 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a | klmk_mjya_mcca
| Stage 9: 48.4Hz | South-Melaka | Melaka-N9 | Malacca | MCCA | 132 | TGBU 1 & 2 | 905 & 1005 | 48.4 | 0 | n/a | n/a | klmk_mjya_mcca
| Stage 9: 48.4Hz | East-Dungun | Kelantan-Terengganu | Kenyir Temporary | KNYT | 132 | KBRG & CHRG/KTGU | 305 & 205 | 48.4 | 0 | n/a | n/a | knyt_chrg | 153 | GBDK, KBRG, KTGU & BRKT
| Stage 9: 48.4Hz | East-Dungun | Kelantan-Terengganu | Chendering | CHRG | 132 | KBRG/KTGU & KNYT/KTGU | 205 & 305 | 48.4 | 0 | n/a | n/a | knyt_chrg
| Stage 9: 48.4Hz | South-Kluang | Johor | Bukit Batu | BBTU | 132 | SNAI & SLNG | 205 & 505 | 48.4 | 0 | n/a | n/a | bbtu_sdai | 232 | SLNG, SNAI, KLAI & UTMJ
| Stage 9: 48.4Hz | South-JB | Johor | Skudai | SDAI | 132 | SNAI & SLNG | 305 & 405 | 48.4 | 0 | n/a | n/a | bbtu_sdai
| Stage 9: 48.4Hz | Selangor | KlangValley | Batang Berjuntai | BTAI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a |  | 14.7682 | BTAI 33kV
| Stage 9: 48.4Hz | KL | KlangValley | K.L.East | KULE | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a |  | 61.6353 | KULE 33kV
| Stage 9: 48.4Hz | KL | KlangValley | KL Pavilion | KLPV | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a |  | 68.7869 | KLPV 33kV
| Stage 9: 48.4Hz | North-Perda | Penang | Tikam Batu | TKBU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a |  | 60.3016 | TKBU 33kV
| Stage 10: 48.3Hz | South-JB | Johor | Tampoi | TPOI | 22 | 132/22kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120 |  | 35.9347 | TPOI 22kV
| Stage 10: 48.3Hz | South-Kluang | Johor | Batu Pahat East | BPHE | 132 | BPHT 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120 | bphe_ygpg | 41 | BPHT, TPCH
| Stage 10: 48.3Hz | South-Kluang | Johor | Yong Peng | YGPG | 132 | BPHT & TPCH | 105 & 205 | 48.3 | 0 | 49.3 | 120 | bphe_ygpg
| Stage 10: 48.3Hz | South-Kluang | Johor | Yong Peng | YGPG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120 |  | - | YGPG 11kV
| Stage 10: 48.3Hz | Selangor | KlangValley | Jalan Meru | MERU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.3 | 0 | 49.3 | 120 |  | 100.9312 | MERU 33 kV
| Stage 10: 48.3Hz | Selangor | KlangValley | Proton | PROT | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120 |  | 115.4056 | PROT 33kV
| Stage 10: 48.3Hz | South-N9 | Melaka-N9 | Kilat | KLAT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120 |  | 21.521 | KLAT 11kV
| Stage 10: 48.3Hz | North-Kedah_Perlis | Kedah-Perlis | Perlis Power Station | PLPS | 132 | TPAU | 705 | 48.3 | 0 | 49.3 | 120 | plps_klps | 96 | TPAU, TEWA, UMKA, KCMT
| Stage 10: 48.3Hz | North-Kedah_Perlis | Kedah-Perlis | Kuala Perlis | KPLS | 132 | TEWA 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120 | plps_klps
| Stage 10: 48.3Hz | Kuala Lumpur | KlangValley | Imbi | IMBI | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120 |  | 91.9517 | IMBI 33 kV
| Stage 10: 48.3Hz | Kuala Lumpur | KlangValley | Kota Damansara | KDSA | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120 |  | 148.4245 | KDSA 33kV
| Stage 10: 48.3Hz | Kuala Lumpur | KlangValley | Galloway | GWAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.3 | 0 | 49.3 | 120 |  | 57.1456 | GWAY 33kV
| Stage 10: 48.3Hz | Perda | Penang | Bukit Tambun | BTBN | 132 | VDOR/JNKO & NBTL Feeders | 105 & 205 | 48.3 | 0 | 49.3 | 120 | btbn_bsri | 144 | JNKO, VDOR, PBTR, NBTL
| Stage 10: 48.3Hz | Perda | Perak | Bagan Serai | BSRI | 132 | PBTR & NBTL | 105 & 205 | 48.3 | 0 | 49.3 | 120 | btbn_bsri
| Stage 11: 48.2Hz | Perda | Penang | Sungai Pinang | SPNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90 |  | 80.5657 | SPNG 33kV
| Stage 11: 48.2Hz | Seremban | Melaka-N9 | Nilai | NLAI | 132 | MTIN & AMID | 505 & 605 | 48.2 | 0 | 49.3 | 90 | nlai_proi_kjng_nuni
| Stage 11: 48.2Hz | Seremban | Melaka-N9 | Paroi | PROI | 132 | MTIN 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90 | nlai_proi_kjng_nuni
| Stage 11: 48.2Hz | Kuala Lumpur | KlangValley | Kajang | KJNG | 132 | KEST 1 & 2 | 105 & 205 | 48.2 | 0 | 49.3 | 90 | nlai_proi_kjng_nuni
| Stage 11: 48.2Hz | Kuala Lumpur | KlangValley | National University | NUNI | 132 | BHGT 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90 | nlai_proi_kjng_nuni
| Stage 11: 48.2Hz | Kuala Lumpur | KlangValley | Bukit Mahkamah | BMKM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90 |  | 51.7312 | BMKM 33kV
| Stage 11: 48.2Hz | Johor Bahru | Johor | Tebrau | TBRU | 132 | PLGI 1 & 2 | 905 & 1005 | 48.2 | 0 | 49.3 | 90 | tbru_psak | 152 | KTGI, UTRM, PUBB, PLGI
| Stage 11: 48.2Hz | Johor Bahru | Johor | Pasak | PSAK | 132 | PUBB & KTGI | 505 & 605 | 48.2 | 0 | 49.3 | 90 | tbru_psak
| Stage 11: 48.2Hz | Kluang | Johor | Renggam | RNGM | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.2 | 0 | 49.3 | 90 |  | 7.3649 | RNGM 11kV
| Stage 11: 48.2Hz | Kluang | Johor | Kluang | KLUG | 132 | KLID & NYOR | 105 & 205 | 48.2 | 0 | 49.3 | 90 |  | 111 | KLID, MSNG, TGMK & NYOR
| Stage 12: 48.1Hz | Alor Setar | Kedah-Perlis | Kangar | KGAR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 |  | 33.8944 | KGAR 11kV
| Stage 12: 48.1Hz | Ipoh | Perak | Sri Iskandar | SIKD | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 & 1W0 | 48.1 | 0 | 49.3 | 60 |  | 30.6965 | SIKD 33kV
| Stage 12: 48.1Hz | Selangor | KlangValley | Ladang Kundang | LKDG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.1 | 0 | 49.3 | 60 |  | 36.7625 | LKDG 33kV
| Stage 12: 48.1Hz | Selangor | KlangValley | Subang Jaya Town Centre | SJTC | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.1 | 0 | 49.3 | 60 |  | 54.0023 | SJTC 33kV
| Stage 12: 48.1Hz | Perda | Penang | Bayan Baru | BBRU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60 |  | 98.3955 | BBRU 33kV
| Stage 12: 48.1Hz | Seremban | Melaka-N9 | Semarak | SMRK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 |  | 22.9899 | SMRK 11kV
| Stage 12: 48.1Hz | Seremban | Melaka-N9 | Semarak | SMRK | 132 | Hualon 1, 2 & 3 | 505605705 | 48.1 | 0 | 49.3 | 60 |  | 40 | HLNN
| Stage 12: 48.1Hz | Johor Bahru | Johor | Seelong | SELG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60 |  | 21.4779 | SELG 11kV
| Stage 12: 48.1Hz | Johor Bahru | Johor | Stulang Darat | STUL | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60 |  | 22.8338 | STUL 22kV
| Stage 12: 48.1Hz | Kluang | Johor | Batu Pahat East | BPHE | 132 | SGAD 1 & 2 | 105 & 205 | 48.1 | 0 | 49.3 | 60 | bphe_sabg | 105 | SGAD, PJML, PYSF, PSRI & SSLG
| Stage 12: 48.1Hz | Ayer Keroh | Johor | Sungai Abong | SABG | 132 | PJML & PYSF | 305 & 405 | 48.1 | 0 | 49.3 | 60 | bphe_sabg
|  | Kuantan | Pahang | Pekan | PKAN | 132 | 132/11kV T1, T2 & T3 | 31, 32 & 33
|  | Dungun | Kelantan-Terengganu | Rantau Petronas | RPTS | 132 | 132/11kV T1 & T2 | 31 & 32
|  | Kluang | Johor | Rengit | RNGT | 132 | 132/11kV T1, T2 & T3 | 31, 32 & 33
|  | Johor Bahru | Johor | Gelang Patah | GPTH | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Ayer Keroh | Melaka-N9 | Pulau Melaka | PMKA | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Kuala Lumpur | KlangValley | Dato Keramat | DKMT | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Johor Bahru | Johor | Danga Bay | DBAY | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Selangor | KlangValley | Elmina West | ELMW | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Kluang | Johor | Pagoh Edu Hub | PGEH | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Kuala Lumpur | KlangValley | Jade Hill | JDHL | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Kuala Lumpur | KlangValley | IOI Mayang | IOIM | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Alor Setar | Kedah-Perlis | Kedah Rubber City | KERC | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Johor Bahru | Johor | Taman Teknologi Johor | TTKJ | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Ipoh | Perak | Parit Buntar | PBTR | 132 | 132/11kV T1 & T2 | 31 & 32
|  | Kuala Lumpur | KlangValley | Damansara Height | DMHT | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Selangor | KlangValley | North Klang Straight | NKST | 132
|  | Kuala Lumpur | KlangValley | Pudu Ulu | PULU | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Kuala Lumpur | KlangValley | Sg Semenyih Waterwork | SSWW | 132
|  | Johor Bahru | Johor | Bandar Penawar | PNWR | 132
|  | Kluang | Johor | Batu Pahat | BPHT | 132
|  | Kluang | Johor | Mersing | MSNG | 132 | 132/11kV T1 & T2 | 31 & 32
|  | Kluang | Johor | Mersing | MSNG | 132 | 132/33kV T3 & T4 | 31 & 32
|  | Kuala Lumpur | KlangValley | KL City Center | KLCC | 132 | 132/11kV T1 & T2 | 31 & 32
|  | Seremban | Melaka-N9 | Tuanku Jaafar Industrial | TJID | 132
|  | Perda | Kedah-Perlis | Sg Petani Industrial | SPID | 132
|  | Kuantan | Pahang | Gebeng | GBNG | 132
|  | Perda | Penang | Bayan Lepas | BLPS | 132 | 132/33kV T1 & T2 | 1T0 & 2T0
|  | Johor Bahru | Johor | Kukup | KKUP | 132
|  | Ayer Keroh | Melaka-N9 | Tangga Batu | TGBU | 132
|  | Dungun | Kelantan-Terengganu | Kertih Industries | KTIH | 132
|  | Kluang | Johor | Peserai | PSRI | 132
|  | Perda | Kedah-Perlis | Gurun East | GRNE | 132
|  | Kuala Lumpur | KlangValley | Cyberjaya North | CBJN | 132
|  | Kuantan | Pahang | Mentakab | MTKB | 132
|  | Seremban | Melaka-N9 | Jementah | JMTH | 132
|  | Kuala Lumpur | KlangValley | Salak South | SLKS | 132
|  | Kuala Lumpur | KlangValley | Mahkota Cheras | MCRS | 132
|  | Ipoh | Perak | Papan | PAPN | 132
|  | Kuala Lumpur | KlangValley | Kampung Pandan | KPDN | 132
|  | Kuala Lumpur | KlangValley | Bukit Jalil Pavillion | PVBJ | 132
|  | Johor Bahru | Johor | Financial Centre | FCTR | 132
|  | Selangor | KlangValley | Penaga | PNGA | 132
|  | Selangor | KlangValley | Ebor | EBOR | 132
|  | Melaka | Melaka-N9 | Sg. Rambai | SRBI | 132
|  | Johor Bahru | Johor | South Key JB | JBSK
|  | Johor Bahru | Johor | Senai Hitec | SHTE
|  | Kuala Lumpur | KlangValley | Ara Damansara | ADAM
|  | Johor Bahru | Johor | Kota Masai | MSAI
|  | Ipoh | Perak | Meru Raya | MERY
|  | Perda | Penang | Tanjung Tokong | TGTK
|  | Kuala Lumpur | KlangValley | MRT Semantan | SMTN
|  | Johor Bahru | Johor | Sedenak | SDNK
|  | Johor Bahru | Johor | Pasir Gudang North | PGPN
|  | Ayer Keroh | Melaka-N9 | Pulau Gadong | PGAD
|  |  | KlangValley | Bukit Serdang | BSRD
|  |  | KlangValley | MRT Cochcrane | COCH
|  |  | Melaka-N9 | Jinjang | JING
|  |  | Melaka-N9 | Senawang | SNWG
|  |  | Perak | Teluk Intan East | TINE
|  |  | KlangValley | Cyberjaya Central | CBJC
|  |  | KlangValley | Matrade | MTRE
|  |  | KlangValley | Menara Warisan | MWSN
|  |  | Johor | Pelangi GIS | PLGI
|  |  | KlangValley | Vallambrosa | VMBR
|  |  | KlangValley | Icon City | ICNC
|  |  | KlangValley | Bukit Bintang City Centre | BBCC
|  |  | KlangValley | Taman Melawati GIS | TMWT
|  |  | Melaka-N9 | Ozana GIS | OZNA
|  |  | KlangValley | Tun Razak Exchange | TRXC

## uvls
Assignment | GM_Subzone | Substation | Mnemonic | kV | Assigned_Feeders | CB | MW Quantum 2024 | Load_Area | Voltage_pickup_setting_(p.u) | Delay(s) | UVLS_Operating_Stage
UVLS Stage 1 | Kuala Lumpur | Kg Chempaka | KCPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 71.7948 | KCPK 33kV | 0.9 | 30 | 1
UVLS Stage 1 | Kuala Lumpur | Segambut | SGBT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 81.4331 | SGBT 33kV | 0.9 | 30 | 1
UVLS Stage 1 | Kuala Lumpur | Manjalara | MJLR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 89.8683 | MJLR 33kV | 0.9 | 30 | 1
UVLS Stage 1 | Johor Bahru | Larkin GIS | LKIN | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 33.3325 | LKIN 22kV | 0.9 | 30 | 1
UVLS Stage 1 | Johor Bahru | Saleng | SLNG | 11 | 132/11kV T1 & T2 | 31 & 32 | 22 | SLNG 11kV | 0.9 | 30 | 1
UVLS Stage 1 | Perda | Bukit Minyak | BMYK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 99.6068 | BMYK 33kV | 0.9 | 30 | 1
UVLS Stage 1 | Perda | Bukit Tengah | BTGH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 90 | BTGH 33kV | 0.9 | 30 | 1
UVLS Stage 1 | Kluang | Mersing | MSNG | 11 | 132/11kV T1 & T2 | 31 & 32 | 10 | MSNG 11kV | 0.9 | 30 | 1
UVLS Stage 2 | Kuala Lumpur | K.L.East | KULE | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 61.6353 | KULE 33kV | 0.9 | 60 | 2
UVLS Stage 2 | Kuala Lumpur | Imbi | IMBI | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 91.9517 | IMBI 33 kV | 0.9 | 60 | 2
UVLS Stage 2 | Kuala Lumpur | Sri Damansara | SDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 67.9905 | SDAM 33kV | 0.9 | 60 | 2
UVLS Stage 2 | Kuala Lumpur | Batu Caves | BCVS | 11 | 132/11kV T1 & T2 | 31 & 32 | 16 | BCVS 11kV | 0.9 | 60 | 2
UVLS Stage 2 | Kuala Lumpur | Harta Kemuncak | HKCK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 90 | HKCK 33kV | 0.9 | 60 | 2
UVLS Stage 2 | Johor Bahru | Majidee | MAJD | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 34.6464 | MAJD 22kV | 0.9 | 60 | 2
UVLS Stage 2 | Johor Bahru | Saleng | SLNG | 33 | 132/33kV T3 &T4 | 3T0 & 4T0 | 22 | SLNG 33kV | 0.9 | 60 | 2
UVLS Stage 2 | Perda | Bukit Tambun | BTBN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 86 | BTBN 33kV | 0.9 | 60 | 2
UVLS Stage 3 | Kuala Lumpur | Harta Kemuncak | HKCK | 11 | 132/11kV T1 & T2 | 31 & 32 | 14 | HKCK 11kV | 0.9 | 90 | 3
UVLS Stage 3 | Kuala Lumpur | Taman Jaya | TJYA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 74 | TJYA 33kV | 0.9 | 90 | 3
UVLS Stage 3 | Kuala Lumpur | Batu Caves | BCVS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 84.9599 | BCVS 33kV | 0.9 | 90 | 3
UVLS Stage 3 | Kuala Lumpur | New SEA Park | NSPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 68.1678 | NSPK 33 kV | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Skudai | SDAI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 26 | SDAI 33kV | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Ulu Tiram | UTRM | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 22 | UTRM 22kV | 0.9 | 90 | 3
UVLS Stage 3 | Johor Bahru | Ulu Tiram | UTRM | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 64 | UTRM 33kV | 0.9 | 90 | 3
UVLS Stage 3 | Selangor | New Rawang | NRWG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 74.945 | NRWG 33 kV | 0.9 | 90 | 3